## Cover
This workbook lists the inputs and assumptions used for NEM market expansion modelling which underpins the Marinus Link Project Assessment Draft Report

## Change log
Version History
Version Number | Date | Description
1 | 2019-12-19 | First public release of Project Marinus 2019 PADR market modelling assumptions.

## Table of Contents
Table of Contents
| Worksheet Name | Worksheet Heading | Description | Primary Source
| Scenarios | Scenarios | Scenario Overview | N/A
| Renewable Energy Zones | Renewable Energy Zones | Geographical map of the Renewable Energy Zones | AEMO 2019 ISP Assumptions Workbook v1.0
| Demand summary | Demand components summary | Demand components chosen for the four scenarios | AEMO Electricity Statement of Opportunities 2018
| Energy forecasts | Annual energy (GWh per annum sent out) | Annual underlying energy forecast for each region for each scenario | N/A - Combination of components described in 'Demand summary' tab
| Rooftop PV forecast | Rooftop PV installed capacity forecast (MW) | Regional Rooftop PV Installed Capacity forecast | AEMO Electricity Statement of Opportunities 2018
| Small non-scheduled PV | Small non-scheduled PV forecast (MW) | Regional existing and new entrant small non-scheduled PV (100 kW – 30 MW) Capacity forecast | AEMO Electricity Statement of Opportunities 2018
| Small non-scheduled Tasmanian hydro | Small non-scheduled Tasmanian hydro generation (GWh) | Historical small non-scheduled Tasmanian hydro generation | NEM-Review
| Battery storage uptake | Behind-the-meter storage uptake (MW and MWh) | Regional behind-the-meter storage uptake | AEMO Electricity Statement of Opportunities 2018
| EV demand forecast | Electric vehicles demand projections (GWh) | Regional electric vehicles demand projections | AEMO Electricity Statement of Opportunities 2018
| DSP | Demand-side participation (MW) | Electricity demand that will be removed from the market when modelled marginal cost reach specified limits | AEMO 2019 ISP Assumptions Workbook v1.0
| Emission Trajectory | Emissions target trajectories | Emission costraints that represents Australia's potential Paris commitment | AEMO 2018 ISP Assumptions Workbook v2.3 (no longer available online)
| VRET | Victorian Renewable Energy Target (VRET) | Renewable energy target to meet VRET | VIC public policy documents
| QRET | Queensland Renewable Energy Target (QRET) | Renewable energy target to meet QRET | QLD public policy documents
| Financial assumptions | Discount Rate | Discount Rates, Value of Customer Reliability | AEMO 2019 ISP Assumptions Workbook v1.2
| Build cost | Build cost ($/kW) real June 2019 dollars | Cost to construct new generation excluding connection costs. | AEMO 2019 ISP Assumptions Workbook v1.0
| Refurbishment | Refurbishment | Refurbishment timings from the 2019 ISP. | AEMO 2019 ISP Assumptions Workbook v1.0
| Retirement | Retirement | End-of-Life, and Retirement Cost | AEMO 2019 ISP Assumptions Workbook v1.0 and AEMO 25 June 2019 Project Expected Retirement Date
| Coal capacity constraint | Coal capacity constraint for Global Slowdown scenario | Coal constraint due to revenue adequacy in lower NEM-wide demand scenario. | Aurora Energy Research analysis of AEMO’s ISP Part 2: economics of coal closures
| Gas prices | Gas prices ($/GJ) real June 2019 dollars | Forecast gas prices | AEMO 2019 ISP Assumptions Workbook v1.0
| Coal prices | Coal prices ($/GJ) real June 2019 dollars | Forecast coal prices | AEMO 2019 ISP Assumptions Workbook v1.0
| Fixed OPEX | Fixed operating cost ($/kW/year) real June 2019 dollars | Power stations' fixed operation and maintenance cost | AEMO 2019 ISP Assumptions Workbook v1.0
| Variable OPEX | Variable operating cost ($/MWh) real June 2019 dollars | Power stations' variable operation and maintenance cost | AEMO 2019 ISP Assumptions Workbook v1.0
| Connection cost | Initial connection costs ($/kW) real June 2019 dollars | Additional build cost that represents proximity to existing network | AEMO 2019 ISP Assumptions Workbook v1.0
| Build limits | Initial build limits (MW) | Modelled limitations impacting build constraints within the expansion modelling | AEMO 2019 ISP Assumptions Workbook v1.0
| Capacity Factors | Capacity Factors | Capacity factors for renewable generators in the renewable energy zones | AEMO Electricity Statement of Opportunities 2018
| Lead time | Lead time (years) | Amount of time from start of simulation before specific technologies that are not already committed/advanced can first be built. | AEMO 2019 ISP Assumptions Workbook v1.0
| Storage properties | Storage properties | Relevant properties of pump hydro and battery storage | AEMO 2019 ISP Assumptions Workbook v1.0
| Mainland hydro storage inflows | Mainland hydro storage inflows (GWh) | Reservoir inflows | AEMO 2019 ISP Assumptions Workbook v1.0
| Tasmanian hydro storage | Tasmanian hydro storage inflows (GWh) | Reservoir schemes and inflows | TasNetworks and Hydro Tasmania
| Prudent Storage Level | Prudent Storage Level for Tasmanian Hydro | Monthly minimum whole-of-system reservoir volume | Hydro Tasmania public documents
| Storage initial level | Storage initial level | Reservoir initial volume and capacities | AEMO 2019 ISP Assumptions Workbook v1.0
| Interconnector capability | Interconnector capability (MW) | Existing notional interconnector limits for Long-term Investment Planning | AEMO 2019 ISP Assumptions Workbook v1.0
| Proportioning factors | Proportioning factors for Inter-Regional losses | Distribution of inter-connector lossess between adjacent regions | AEMO 2019 ISP Assumptions Workbook v1.0
| Augmentations | Augmentations | QNI augmentation options | AEMO 2019 ISP Assumptions Workbook v1.0
| Generator capacity | Generator capacity | Maximum capacity is used to report capacity factors and calculate fixed operating costs. It may not correspond to "installed capacity" listed in Generation Information workbooks, when maximum seasonal ratings differ. Generator capacity may vary with weather conditions. The ISP uses AEMO Generation Information page (2017 December release) for seasonal ratings for the first 10 years of the model period. Not all committed or advanced projects have ratings listed in Generation Information. Where information is absent Maximum Capacity is used. This will be updated with the most recent information from the AEMO Generation Information Page. | AEMO 2019 ISP Assumptions Workbook v1.0
| Generation limits | Generator modelling assumptions | Generator minimum capacities, minimum and maximum capacity factors | AEMO 2019 ISP Assumptions Workbook v1.0
| Seasonal ratings | Seasonal ratings | Generator seasonal ratings | AEMO 2019 ISP Assumptions Workbook v1.0
| Generator reliability settings | Generator reliability settings | Generator technology forced outage parameters | AEMO 2019 ISP Assumptions Workbook v1.0
| Maintenance | Maintenance rate | Generator technology maintenance outage parameters | AEMO 2019 ISP Assumptions Workbook v1.0
| Heat rates | Heat rates | Generator heat rates | AEMO 2019 ISP Assumptions Workbook v1.0
| Auxiliary | Auxiliary load | Generator auxiliary load | AEMO 2019 ISP Assumptions Workbook v1.0
| Emissions | Emissions | Generator emission rates | AEMO 2019 ISP Assumptions Workbook v1.0
| Reserve | Regional reserve | Minimum reserve levels for reliable regional supply | AEMO 2019 ISP Assumptions Workbook v1.0
| Mainland inertia | Mainland inertia | Minimum inertia levels to meet minimum requirements for mainland regions | Inertia requirements methodology: Inertia requirements and shortfalls
| Tasmanian inertia | Tasmanian inertia | Minimum inertia levels to meet minimum requirements for Tasmania | TasNetworks
|  |  | Hyperlinks | Can modify to local path
|  |  | AEMO Feb 2019 ISP Assumptions Workbook v1.0 | https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Inputs-Assumptions-and-Methodologies
|  |  | AEMO Electricity Statement of Opportunities 2018 | https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/NEM-Electricity-Statement-of-Opportunities
|  |  | NEM-Review | http://v6.nem-review.info/what/index.aspx/
|  |  | VIC public policy documents | https://www.energy.vic.gov.au/renewable-energy/victorias-renewable-energy-targets
|  |  | QLD public policy documents | https://www.dnrme.qld.gov.au/energy/initiatives/powering-queensland
|  |  | AEMO Sept 2019 ISP Assumptions Workbook v1.2 | https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Inputs-Assumptions-and-Methodologies
|  |  | Hydro Tasmania public documents | https://www.hydro.com.au/clean-energy/secure-energy
|  |  | Aurora Energy Research analysis of AEMO’s ISP Part 2: economics of coal closures | https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Integrated-System-Plan/2018-Integrated-System-Plan
|  |  | Inertia requirements methodology: Inertia requirements and shortfalls | https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Inputs-Assumptions-and-Methodologies

## Scenarios
TOC
Scenarios
| Assumptions | Global Slowdown scenario | Status Quo scenario | Sustained Renewables Uptake scenario | Accelerated Transition to a Low Emissions Future scenario
Consumption forecast and consumer behaviour
| Underlying consumption | AEMO 2018 ESOO Weak, with Tasmanian load reduced by 240 MW from 2025-26, rather than 78 MW. | 2018 AEMO ESOO Neutral |  | 2018 AEMO ESOO Strong
| Rooftop PV | 2018 AEMO ESOO Weak | 2018 AEMO ESOO Neutral |  | 2018 AEMO ESOO Strong
| Small non-scheduled PV (100 kW – 30 MW) | 2018 AEMO ESOO Weak | 2018 AEMO ESOO Neutral |  | 2018 AEMO ESOO Strong
| Domestic storage MW and MWh | 2018 AEMO ESOO Weak | 2018 AEMO ESOO Neutral |  | 2018 AEMO ESOO Strong
| Demand-side participation (DSP) | 2018 AEMO ISP Weak | 2018 AEMO ISP Neutral |  | 2018 AEMO ISP Strong
| Electric vehicles | 2018 AEMO ESOO Weak | 2018 AEMO ESOO Neutral |  | 2018 AEMO ESOO Strong
| Value of customer reliability (VCR) | Aggregate NEM wide value of $33,460/MWh
Climate and energy policies
| Emission reduction policy | Not explicitly modelled. | The electricity sector has been modelled to achieve at least a 28 % reduction in emissions compared to 2005 levels by 2030. Post 2030, a linear reduction of emissions to 70 % reduction compared to 2016 levels by 2050. |  | The electricity sector has been modelled to achieve at least a 52 % reduction in emissions compared to 2005 levels by 2030. Post 2030, a linear reduction of emissions to 90 % reduction compared to 2016 levels by 2050.
| Victorian Renewable Energy Target (VRET) 2020 | Target of 25 % of Victorian demand from renewables by calendar year 2020
| VRET 2025 | Not explicitly modelled | Target of 40 % of Victorian demand from renewables by calendar year 2025
| VRET 20230 | Not explicitly modelled | Target of 50 % of Victorian demand from renewables by calendar year 2030
| Queensland Renewable Energy Target (QRET) 2030 | Not explicitly modelled | Target of 50 % of Queensland demand from renewables by calendar year 2030
Generator retirements
| Economic retirement | Allowed for thermal generators if it is least-cost to do so
| Fixed date thermal retirements (excluding South Australian gas-fired generators – listed separately) | Based on end of technical life as per AEMO’s February 2019 planning and forecasting assumptions workbook. Where station specific information was available, retirement dates were updated as per the AEMO Project Expected Retirement Date workbook published 25 June 2019. |  | Based on end of technical life as per AEMO’s February 2019 planning and forecasting assumptions workbook. Where station specific information was available, retirement dates were updated as per the AEMO Project Expected Retirement Date workbook published 25 June 2019 except coal-fired units are generally assumed to retire three to five years earlier. | Based on end of technical life as per AEMO’s February 2019 planning and forecasting assumptions workbook. Where station specific information was available, retirement dates were updated as per the AEMO Project Expected Retirement Date workbook published 25 June 2019.
| NEM-wide coal capacity restriction | In line with the lower NEM-wide demand scenario from Aurora Energy Research’s revenue adequacy report to AEMO83, thermal coal retirement commences from 2025 and is accelerated by 3-5 GW from Status Quo scenario. | Not explicitly modelled.
| South Australian gas retirements | Torrens Island A and Torrens Island B are assumed to retire in the year that Project EnergyConnect is commissioned, as per the ElectraNet PACR. Osborne power station and Pelican Point power station are assumed to retire in 2023-24 and 2037-38, respectively, as per the AEMO Project Expected Retirement Dates from 25 June 2019. Pelican Point power station is not allowed to retire economically prior to Project EnergyConnect to maintain system strength in South Australia.
| Fixed date non-thermal retirements | End of technical life as per the AEMO Project Expected Retirement Date workbook published 25 June 2019.
Fuel supply forecast
| Coal fuel cost | AEMO Feb 2019 Neutral forecast
| Gas fuel cost | AEMO Feb 2019 Slow Change forecast | AEMO Feb 2019 Neutral forecast |  | AEMO Feb 2019 Fast Change forecast
Generation technology cost projections
| New entrant generation technology cost projections for wind, solar PV SAT, OCGT, CCGT, PSH and large-scale battery storage | AEMO Feb 2019 ‘4 degree’ scenario |  |  | AEMO Feb 2019 ‘2 degree’ scenario. ‘4 degree’ scenario for PSH.
Industry developments
| Snowy 2.0 | Commissioned 2029-30 | Commissioned 2026-27
| VNI Option 1 (Dederang-Lower Tumut path) | Commissioned 2029-30 | Commissioned 2022-23
| Western Victoria RIT-T augmentation | The ISP 2018 preferred option is assumed commissioned by 2023-24
| QNI-Option 3A | Commissioned 2023-24
| Project EnergyConnect | Commissioned 2024-25
| KerangLink | The preferred KerangLink ISP 2018 option is assumed to be commissioned in 2032-33, aligning with the assumed fixed date retirement of the fourth unit of Yallourn. | The preferred KerangLink ISP 2018 option is assumed to be commissioned in 2030-31 aligning with the assumed fixed date retirement of the second unit of Yallourn. | The preferred KerangLink ISP 2018 option is assumed to be commissioned in 2027-28 aligning with the assumed fixed date retirement of the second unit of Yallourn. | The preferred KerangLink ISP 2018 option is assumed to be commissioned in 2029-30, aligning with the assumed fixed date retirement of the first unit of Yallourn.

## Renewable Energy Zones
TOC
| Renewable Energy Zones |  |  |  |  | Renewable Energy Zone Map | NEM Regional Cost Zone Map
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
As used in the AEMO Feb 2019 ISP
| # | Name | NEM Region | NEM Zone | Regional Cost Zones
| 1 | Far North Queensland | QLD | NQ | Low
| 2 | North Queensland Clean Energy Hub | QLD | NQ | Medium
| 3 | Northern Queensland | QLD | NQ | Low
| 4 | Isaac | QLD | NQ | Low
| 5 | Barcaldine | QLD | CQ | Medium
| 6 | Fitzroy | QLD | CQ | Low
| 7 | Darling Downs | QLD | SWQ | Low1
| 8 | North West New South Wales | NSW | NNS | Medium
| 9 | New England | NSW | NNS | Low
| 10 | Central West New South Wales | NSW | NCEN | Medium
| 11 | Southern New South Wales Tablelands | NSW | CAN | Low
| 12 | Cooma-Monaro | NSW | CAN | Medium
| 13 | Tumut | NSW | CAN | Medium
| 14 | South West New South Wales | NSW | SWNSW | High
| 15 | Broken Hill | NSW | SWNSW | High
| 16 | Murray River (NSW) | NSW | SWNSW | High
|  | Murray River (VIC) | VIC | NVIC | High
| 17 | Western Victoria | VIC | CVIC | Medium2
| 18 | Moyne | VIC | MEL | Medium2
| 19 | Ovens Murray | VIC | NVIC | Medium2
| 20 | Gippsland | VIC | LV | Medium
| 21 | South East South Australia | SA | SESA | Medium2
| 22 | Riverland (SA) | SA | NSA | Medium
|  | Riverland (NSW) | NSW | SWNSW | High
| 23 | Mid-North South Australia | SA | NSA | Low1
| 24 | Yorke Peninsula | SA | NSA | Low
| 25 | Northern South Australia | SA | NSA | Medium
| 26 | Leigh Creek | SA | NSA | Medium1
| 27 | Roxby Downs | SA | NSA | Medium1
| 28 | Eastern Eyre Peninsula | SA | NSA | Medium
| 29 | Western Eyre Peninsula | SA | NSA | Medium
| 30 | North West Tasmania | TAS | TAS | Medium2
| 31 | Tasmania Midlands | TAS | TAS | Medium2
| 32 | North East Tasmania | TAS | TAS | Medium1
Note:
1 When a REZ zone covers two regional cost zones, the lower cost zone is utilised
2 When a REZ zone covers all three regional cost zones, the medium cost zone is utilised
3 The same cost zone is applied to both sides of a REZ that straddles NEM regions.

## Demand summary
TOC
Demand components summary
| Primary source: AEMO Electricity Statement of Opportunities 2018 |  | AEMO's forecasting data portal
AEMO Feb 2019 ISP demand scenarios
| Demand component | Slow scenario | Neutral scenario | Fast scenario
| Underlying demand | 2018 ESOO Weak | 2018 ESOO Neutral | 2018 ESOO Strong
| Rooftop PV | 2018 ESOO Neutral | 2018 ESOO Neutral | 2018 ESOO Neutral
| Small non-scheduled PV (100 kW - 300 MW) | 2018 ESOO Neutral | 2018 ESOO Neutral | 2018 ESOO Neutral
| EV uptake | 2018 ESOO Weak | 2018 ESOO Neutral | 2018 ESOO Strong
| Domestic storage MW and MWh | 2018 ESOO Neutral | 2018 ESOO Neutral | 2018 ESOO Neutral
| Tasmanian small non-scheduled Hydro | N/A | N/A | N/A
Project Marinus 2019 PADR scenarios
| Demand component | Global Slowdown scenario | Status Quo scenario | Sustained Renewables Uptake scenario | Accelerated Transition scenario
| Underlying demand | 2018 ESOO Weak1 | 2018 ESOO Neutral | 2018 ESOO Neutral | 2018 ESOO Strong
| Rooftop PV | 2018 ESOO Weak | 2018 ESOO Neutral | 2018 ESOO Neutral | 2018 ESOO Strong
| Small non-scheduled PV (100 kW - 300 MW) | 2018 ESOO Weak2 | 2018 ESOO Neutral2 | 2018 ESOO Neutral2 | 2018 ESOO Strong2
| EV uptake | 2018 ESOO Weak | 2018 ESOO Neutral | 2018 ESOO Neutral | 2018 ESOO Strong
| Domestic storage MW and MWh | 2018 ESOO Weak | 2018 ESOO Neutral | 2018 ESOO Neutral | 2018 ESOO Strong
| Small non-scheduled Tasmanian Hydro3 | Historical generation added back to demand | Historical generation added back to demand | Historical generation added back to demand | Historical generation added back to demand
1. The 2018 ESOO Slow demand forecast is intended to represent a scenario where economic growth is weak, leading to a reduction in business investment and resulting in some industrial closures. The forecast therefore assumes that Boyne Island smelter (826 MW) in QLD, Tomago smelter (930 MW) in NSW and Portland smelter (480 MW) in VIC are retired during the 2020s. These closures significantly reduce the expected regional demand. In comparison, the load reduction for Tasmania is relatively minor for the Slow demand forecast (approximately 78 MW). Therefore, for the Project Marinus PADR it has been assumed that two industrial closures occur, totalling approximately 240 MW (an additional 162 MW compared to the 2018 ESOO Weak forecast, which is approximately 1,419 GWh annually).
2. Capacity from explicitly modelled small non-scheduled PV generators is netted off the AEMO 2018 ESOO forecast. This includes Griffith Solar Farm, Hughenden Solar Farm and Longreach Solar Farm.
3. Small non-scheduled Tasmanian Hydro are explicitly modelled using the 10 pond scheme described in this workbook. Therefore, their historical generation, which AEMO has subtracted from the forecast demand in the 2018 ESOO data, has been added back onto demand (approximately 460 GWh annually).

## Energy forecasts
TOC
Annual energy (GWh per annum sent out)
Primary source: N/A - Combination of components described in 'Demand summary' tab
Targets shown are 'Underlying (that is, equivalent to the 'power point' - gross of rooftop PV generation and other small non-scheduled systems), sent-out'
| Stong: | To be used in Accelerated Transition to a Low Emissions Future scenario
| Neutral: | To be used in Status Quo scenario and Sustained Renewables Uptake scenario
| Weak: | To be used in Global Slowdown scenario
| Underlying energy (GWh p.a. sent-out) | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Historical profile | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
| Stong NSW | 71184.0079 | 71404.0072 | 72161.9993 | 72767.8739 | 74089.0019 | 75681.9971 | 77420.991 | 79346.2385 | 81217.5913 | 83273.4675 | 85316.0131 | 87008.3305 | 88977.0078 | 90975.0104 | 92962.9254 | 95041.069 | 97101.0106 | 99188.0036 | 101330.4181 | 103594.6619 | 104864.3841 | 106198.6067 | 107531.0063 | 108928.478 | 110195.8102 | 111526.3721 | 112859.7628 | 114260.5516 | 115526.4035 | 116858.8128
| Stong QLD | 54792.0028 | 56611.4431 | 57186.4405 | 57668.4361 | 58710.4375 | 59375.4495 | 60473.0007 | 61363.8359 | 62237.7347 | 63165.6657 | 63988.9995 | 64950.5942 | 65420.9991 | 66295.0006 | 67239.2944 | 68340.2585 | 69307.0034 | 70345.0007 | 71441.7964 | 72659.0183 | 73787.8156 | 74299.1996 | 74808.9991 | 75393.9507 | 75828.5989 | 76336.993 | 76846.7719 | 77434.7128 | 77867.7941 | 78377.5997
| Stong SA | 13882.9907 | 14423.9993 | 14581.0006 | 14645.1822 | 14865.0006 | 15018.9999 | 15293.0004 | 15591.1759 | 15905.9232 | 16214.904 | 16502.0014 | 16788.7303 | 17093.0011 | 17280.9968 | 17582.8072 | 17873.0665 | 18172.0022 | 18497.0009 | 18812.801 | 19144.4303 | 19466.0628 | 19811.2236 | 19966.9998 | 20136.2151 | 20279.6026 | 20435.0211 | 20590.8189 | 20760.6729 | 20903.8014 | 21059.5856
| Stong TAS1 | 11328.6927 | 11422.9787 | 11428.3314 | 11571.4397 | 11616.3079 | 11651.4492 | 11796.4546 | 12033.6562 | 12181.7297 | 12248.249 | 12283.9932 | 12511.5479 | 12604.7348 | 12777.3769 | 12920.1855 | 13157.6428 | 13330.6034 | 13481.2908 | 13561.4755 | 13827.5123 | 13921.1931 | 14112.687 | 14290.3727 | 14564.4453 | 14739.7969 | 14848.5761 | 14891.9712 | 15117.5331 | 15172.7978 | 15323.235
| Stong VIC | 47360.8854 | 48117.8741 | 49014.8777 | 49506.8498 | 50737.8729 | 51613.892 | 53049.8804 | 54658.7919 | 56343.4908 | 58083.3796 | 59799.8786 | 61441.0709 | 63179.8779 | 64938.877 | 66678.8612 | 68472.3338 | 70155.8811 | 71862.8818 | 73692.8826 | 74834.4788 | 75892.3597 | 76994.877 | 78095.8777 | 79239.6321 | 80296.89 | 81396.2621 | 82497.2383 | 83644.2856 | 84699.8746 | 85800.8767
| Neutral NSW | 71318.3461 | 71714.0508 | 71555.6502 | 72101.7909 | 72996.3163 | 74088.1771 | 75234.279 | 76428.2292 | 77685.3601 | 79169.9457 | 80661.4324 | 81991.9219 | 83168.1358 | 84552.2193 | 85914.8379 | 87273.5975 | 88627.9027 | 89976.3445 | 91387.019 | 92888.2863 | 94332.7175 | 95874.0049 | 97461.0101 | 99159.3127 | 100792.0122 | 102538.1879 | 103421.1858 | 104371.2833 | 105188.0036 | 106071.0138
| Neutral QLD | 54175.5668 | 54782.3028 | 55379.8724 | 55990.1937 | 56474.0204 | 56836.0214 | 57193.8289 | 57762.0238 | 58321.0709 | 58993.4793 | 59687.9971 | 60356.5032 | 60960.8808 | 61602.8842 | 62283.4393 | 63053.6197 | 63672.2084 | 64326.0027 | 65048.3989 | 65858.5025 | 66584.4413 | 67402.6029 | 68254.9937 | 69209.996 | 70074.8018 | 71046.0023 | 72062.2988 | 72529.6615 | 72853.4032 | 73248.8038
| Neutral SA | 13795.4853 | 14262.3309 | 14296.8765 | 14396.3925 | 14524.9733 | 14416.9467 | 14350.0418 | 14501.1209 | 14624.0288 | 14790.5637 | 14984.1674 | 15137.5045 | 15323.4995 | 15378.4872 | 15554.8037 | 15721.445 | 15880.9897 | 16058.1997 | 16228.2013 | 16407.9096 | 16578.3963 | 16764.821 | 16959.0016 | 17172.4815 | 17375.4045 | 17597.2881 | 17829.462 | 18086.28 | 18140.2042 | 18206.3899
| Neutral TAS1 | 11265.5012 | 11321.584 | 11140.0728 | 11275.7389 | 11290.2924 | 11243.4608 | 11196.2001 | 11353.7209 | 11411.7427 | 11394.0944 | 11332.2562 | 11481.9162 | 11496.3442 | 11584.1503 | 11651.9241 | 11797.29 | 11873.9698 | 11925.9032 | 11913.6754 | 12085.2733 | 12084.8293 | 12179.487 | 12259.3726 | 12432.7336 | 12508.1969 | 12570.221 | 12568.8121 | 12750.8105 | 12763.9976 | 12875.6348
| Neutral VIC | 46736.8235 | 47338.9013 | 47588.9837 | 48110.9506 | 48938.8215 | 49082.8399 | 49322.3883 | 50291.848 | 51205.1532 | 52203.4585 | 53296.0737 | 54496.7336 | 55736.6632 | 56959.9567 | 58157.2065 | 59327.0723 | 60411.8921 | 61478.2936 | 62666.6848 | 63921.8222 | 65153.1754 | 66460.0799 | 67809.8838 | 69248.0676 | 69930.4945 | 70651.84 | 71374.6213 | 72139.5361 | 72820.6814 | 73543.48
| Weak NSW | 71561.0061 | 71790.0084 | 72216.0216 | 70625.0286 | 71217.0028 | 71938.9931 | 72643.0052 | 73293.6684 | 70973.9742 | 68327.9572 | 65627.0813 | 64834.6972 | 65051.0039 | 65887.0133 | 66819.7005 | 67725.4708 | 68597.0088 | 69475.0059 | 70429.8161 | 71440.2783 | 72454.5421 | 73531.206 | 74652.0094 | 75846.4608 | 77038.6104 | 78308.0335 | 79634.705 | 81060.1311 | 82471.8047 | 82934.6183
| Weak QLD | 52853.004 | 52972.0016 | 53308.0207 | 53075.0657 | 52887.0065 | 52355.9974 | 52292.0043 | 52234.4063 | 44573.9522 | 44574.9639 | 44077.9963 | 44613.6461 | 44779.002 | 45336.006 | 46005.805 | 46625.5461 | 47172.0039 | 47733.0019 | 48376.3981 | 49078.7904 | 49741.611 | 50467.6071 | 51223.9906 | 52050.1653 | 52833.8016 | 53691.3292 | 54586.6386 | 55569.5872 | 56503.3985 | 56849.8075
| Weak SA | 13450.9883 | 13898.0011 | 13795.0015 | 13579.023 | 13646.0005 | 13474.0009 | 13405.9984 | 13465.1442 | 13524.9978 | 13471.9881 | 13281.0072 | 12987.5563 | 13038.0053 | 12998.0008 | 13108.9419 | 13190.3834 | 13277.0029 | 13383.0025 | 13478.0448 | 13580.8009 | 13674.7756 | 13784.7534 | 13901.8364 | 14037.2374 | 14162.7482 | 14306.3078 | 14460.333 | 14635.8239 | 14799.3929 | 14985.1163
| Weak TAS1, 2 | 10785.6927 | 10800.9788 | 10622.3212 | 10551.3946 | 10509.3274 | 8322.2891 | 8340.2943 | 8433.2361 | 8463.5936 | 8313.1098 | 7951.8315 | 7744.8757 | 7603.5812 | 7625.2187 | 7509.0583 | 7575.8185 | 7593.4682 | 7581.113 | 7483.8623 | 7565.2872 | 7488.3867 | 7501.7963 | 7500.6978 | 7588.0384 | 7589.9363 | 7573.2182 | 7492.9752 | 7589.7015 | 7532.0046 | 7566.2753
| Weak VIC | 46782.8872 | 45030.8919 | 42814.9159 | 42021.9608 | 42595.8716 | 42369.8838 | 42530.8752 | 43119.5344 | 43697.8599 | 43864.8228 | 43454.882 | 43271.649 | 44103.8783 | 44989.8807 | 45940.5705 | 46787.0954 | 47600.8809 | 48405.8839 | 49315.8879 | 50274.1048 | 51240.1303 | 52259.88 | 53317.8815 | 54441.0077 | 55565.8846 | 56759.638 | 58003.5187 | 58512.9847 | 58964.8827 | 59443.8793
1. Small non-scheduled Tasmanian Hydro are explicitly modelled using the 10 pond scheme described in this workbook. Therefore, their historical generation, which AEMO has subtracted from the forecast demand in the 2018 ESOO data, has been added back onto demand (approximately 460 GWh annually).
2. The 2018 ESOO Slow demand forecast is intended to represent a scenario where economic growth is weak, leading to a reduction in business investment and resulting in some industrial closures. The forecast therefore assumes that Boyne Island smelter (826 MW) in QLD, Tomago smelter (930 MW) in NSW and Portland smelter (480 MW) in VIC are retired during the 2020s. These closures significantly reduce the expected regional demand. In comparison, the load reduction for Tasmania is relatively minor for the Slow demand forecast (approximately 78 MW). Therefore, for the Project Marinus PADR it has been assumed that two industrial closures occur, totalling approximately 240 MW (an additional 162 MW compared to the 2018 ESOO Weak forecast, which is approximately 1,419 GWh annually).

## Rooftop PV forecast
TOC
Rooftop PV installed capacity forecast (MW)
| Primary source: AEMO Electricity Statement of Opportunities 2018 | AEMO's forecasting data portal
| Stong: | To be used in Accelerated Transition to a Low Emissions Future scenario
| Neutral: | To be used in Status Quo scenario and Sustained Renewables Uptake scenario
| Weak: | To be used in Global Slowdown scenario
| Scenario and Region | AEMO forecast
| Capacity (MW) | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Historical profile | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
| Stong NSW | 3793.9 | 3892.25 | 3998.47 | 4206.36 | 4355.02 | 4604.69 | 4806.5 | 5018.05 | 5241.71 | 5475.13 | 5720.3 | 6208.24 | 6927.99 | 7705.02 | 8378.66 | 8674.4 | 8997.47 | 9349.15 | 9732.66 | 10173.3 | 10624.94 | 11084.32 | 11556.65 | 12044.15 | 12569.27 | 12951.04 | 13301.06 | 13670.27 | 14029.79 | 14385.93
| Stong QLD | 3328.85 | 3417.79 | 3511.87 | 3623.07 | 3730.15 | 3959.42 | 4154.49 | 4359.83 | 4577.91 | 4806.45 | 5047.67 | 5428.99 | 5906.07 | 6368.17 | 6809.67 | 7064.93 | 7333.99 | 7617.57 | 7916.87 | 8238 | 8571.47 | 8916.93 | 9276.16 | 9650.2 | 10045.16 | 10329.43 | 10613.66 | 10910.99 | 11214.98 | 11527.5
| Stong SA | 1316.85 | 1338.14 | 1360.34 | 1389.12 | 1415.3 | 1483.29 | 1543.7 | 1606.85 | 1673.46 | 1742.73 | 1815.31 | 1941.65 | 2102.65 | 2260.84 | 2404.01 | 2482.52 | 2565.99 | 2654.54 | 2747.12 | 2846.25 | 2947.77 | 3051.25 | 3157.55 | 3266.98 | 3382.75 | 3461.75 | 3537.12 | 3616.03 | 3694.74 | 3774.24
| Stong TAS | 226.16 | 228.42 | 230.28 | 237 | 240.67 | 251.18 | 260.25 | 269.69 | 279.64 | 289.9 | 306.57 | 341.41 | 389.16 | 438.26 | 478.99 | 494.86 | 512.32 | 528.81 | 547.03 | 568.6 | 590.15 | 611.48 | 632.87 | 654.43 | 677.45 | 691.54 | 703.2 | 715.31 | 725.76 | 734.99
| Stong VIC | 2901.6 | 2978.68 | 3054.41 | 3225.48 | 3484.36 | 3685.99 | 3859.21 | 4041.25 | 4234.16 | 4435.99 | 4650.76 | 5168.79 | 5849.15 | 6557.54 | 7168.92 | 7438.64 | 7725.57 | 8030.28 | 8349.36 | 8704.54 | 9067.39 | 9434.42 | 9811.02 | 10199.4 | 10620.7 | 10915.34 | 11181.36 | 11461.92 | 11738.44 | 12016.05
| Neutral NSW | 3434.98 | 3500.83 | 3568.62 | 3638.33 | 3710.07 | 3903.36 | 4051.55 | 4206.33 | 4369.82 | 4539.52 | 4717.26 | 4939.03 | 5171.61 | 5467.13 | 5932.14 | 6088.64 | 6244.01 | 6398.2 | 6553.12 | 6708.75 | 6863.01 | 7012.81 | 7161.5 | 7310.16 | 7473.33 | 7629.69 | 7759.14 | 7896.05 | 8039.28 | 8192.93
| Neutral QLD | 3065.32 | 3129.74 | 3196.04 | 3264.28 | 3334.58 | 3524.5 | 3680.53 | 3844.17 | 4017.61 | 4198.62 | 4389.04 | 4623.18 | 4870.17 | 5143.75 | 5503.25 | 5642.13 | 5783.42 | 5928.38 | 6079.76 | 6231.53 | 6386.91 | 6543.54 | 6702.5 | 6864.08 | 7038.29 | 7211.39 | 7368.96 | 7534.41 | 7705.52 | 7885.36
| Neutral SA | 1249.67 | 1262.11 | 1274.9 | 1288.04 | 1301.59 | 1357.6 | 1405.64 | 1455.67 | 1508.45 | 1563.07 | 1620.17 | 1692.07 | 1767.25 | 1846.38 | 1944.1 | 1976.47 | 2009.06 | 2041.79 | 2074.77 | 2107.98 | 2140.97 | 2173.48 | 2206.01 | 2238.73 | 2273.83 | 2308.21 | 2338.69 | 2370.39 | 2402.6 | 2435.97
| Neutral TAS | 219.02 | 220.1 | 221.2 | 222.36 | 223.55 | 232.45 | 239.85 | 247.55 | 260.3 | 271.75 | 283.57 | 300.37 | 317.57 | 335.41 | 361.82 | 368.54 | 375.34 | 382.34 | 389.65 | 397.15 | 404.34 | 411.09 | 417.58 | 423.83 | 430.72 | 437.03 | 441.54 | 446.28 | 450.92 | 455.69
| Neutral VIC | 2722.86 | 2777.11 | 2832.9 | 2890.33 | 2949.4 | 3107.83 | 3235.95 | 3371.17 | 3563.75 | 3735.05 | 3926.39 | 4182.48 | 4458.09 | 4772.7 | 5209.71 | 5365.87 | 5525.62 | 5688.44 | 5856.38 | 6027.73 | 6198.25 | 6365.45 | 6532.34 | 6699.77 | 6882.9 | 7059.7 | 7208.89 | 7366.51 | 7528.67 | 7699.8
| Weak NSW | 2354.7 | 2396.56 | 2439.58 | 2483.76 | 2529.19 | 2623.11 | 2682.44 | 2744.1 | 2807.18 | 2872.39 | 2939.13 | 3029.76 | 3123.17 | 3219.49 | 3318.82 | 3359.53 | 3401.04 | 3443.27 | 3486.2 | 3530.03 | 3638.24 | 3826.15 | 4026.69 | 4242.68 | 4476.74 | 4730.82 | 5003.83 | 5295.6 | 5606.06 | 5934.85
| Weak QLD | 2601.26 | 2658.5 | 2716.94 | 2770.29 | 2828.87 | 2954.48 | 3040.44 | 3127.77 | 3213.81 | 3302.56 | 3393.85 | 3513.91 | 3638.21 | 3766.9 | 3900.17 | 3959.75 | 4020.4 | 4082.16 | 4145.06 | 4209.17 | 4281.9 | 4371.2 | 4466.42 | 4567.29 | 4711.06 | 4897.61 | 5101.77 | 5328.45 | 5569.46 | 5823.66
| Weak SA | 1006.75 | 1017.14 | 1028.61 | 1038.88 | 1048.32 | 1079.52 | 1104.3 | 1127.64 | 1150.94 | 1174.64 | 1199.03 | 1233.19 | 1268.3 | 1304.42 | 1341.57 | 1354.23 | 1367.07 | 1380.12 | 1393.36 | 1406.83 | 1421 | 1459.64 | 1504.02 | 1548.95 | 1595.26 | 1644.35 | 1695.92 | 1749.52 | 1803.88 | 1858.91
| Weak TAS | 156.08 | 156.68 | 157.28 | 157.89 | 158.53 | 162.34 | 164.95 | 167.65 | 170.43 | 173.27 | 176.17 | 180.46 | 184.86 | 189.37 | 194 | 194.87 | 200.24 | 205.46 | 211.54 | 218.95 | 227.71 | 240.64 | 254.04 | 268.11 | 282.98 | 298.32 | 313.96 | 329.93 | 345.7 | 361.34
| Weak VIC | 1889.08 | 1923.55 | 1958.99 | 1995.09 | 2032.27 | 2109.78 | 2163.03 | 2218.63 | 2275.57 | 2334.43 | 2394.5 | 2474.73 | 2557.63 | 2643.32 | 2731.88 | 2775.1 | 2850.97 | 2933.07 | 3021.8 | 3117.81 | 3245.68 | 3435.38 | 3641.83 | 3867.35 | 4112.38 | 4376.43 | 4657.74 | 4956.78 | 5270.68 | 5600.09

## Small non-scheduled PV
TOC
Small non-scheduled PV forecast (MW)
| Primary source: AEMO Electricity Statement of Opportunities 2018 | AEMO's forecasting data portal
| Stong: | To be used in Accelerated Transition to a Low Emissions Future scenario
| Neutral: | To be used in Status Quo scenario and Sustained Renewables Uptake scenario
| Weak: | To be used in Global Slowdown scenario
| Scenario and Region | AEMO forecast
| Capacity (MW) | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Historical profile | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
| Stong NSW1 | 260.91 | 323.62 | 385.03 | 445.8 | 505.48 | 563.07 | 616.67 | 667.66 | 716.85 | 767.2 | 796.04 | 828.91 | 843.34 | 861.12 | 879.91 | 898.51 | 942.66 | 986.82 | 1031.2 | 1076.26 | 1121.95 | 1168.2 | 1214.96 | 1262.21 | 1310.06 | 1358.41 | 1406.93 | 1455.67 | 1504.41 | 1552.96
| Stong QLD2 | 270.01 | 364.66 | 455.52 | 545.43 | 632.75 | 717.51 | 802.38 | 890.02 | 982.61 | 1081.77 | 1185.45 | 1294.68 | 1408.86 | 1525.06 | 1642.34 | 1755.11 | 1863.31 | 1968.11 | 2069.26 | 2169.34 | 2268.27 | 2365.91 | 2462.21 | 2557.13 | 2650.96 | 2743.49 | 2834.16 | 2923.11 | 3010.52 | 3096.71
| Stong SA | 79.29 | 105.11 | 129.19 | 152.4 | 175.59 | 197.95 | 218.85 | 239.49 | 260.09 | 281.37 | 287.7 | 302.79 | 319.88 | 338.5 | 357.81 | 377.12 | 396.53 | 416.16 | 436.01 | 456.2 | 476.7 | 497.47 | 518.5 | 539.77 | 561.33 | 583.14 | 605.04 | 627.06 | 649.09 | 671.05
| Stong TAS | 11.84 | 13.41 | 14.86 | 26.45 | 37.78 | 46.98 | 55.41 | 54.86 | 54.31 | 53.76 | 53.23 | 52.69 | 52.17 | 51.65 | 51.13 | 50.62 | 51.71 | 52.85 | 54.04 | 67.25 | 81.06 | 95.46 | 110.44 | 126.01 | 142.21 | 159 | 176.31 | 194.15 | 212.34 | 230.73
| Stong VIC | 94.5 | 97.76 | 112.18 | 126.63 | 141.73 | 156.22 | 170.48 | 185.22 | 200.54 | 216.67 | 234.49 | 253.9 | 274.89 | 297.01 | 319.85 | 342.64 | 365.39 | 388.05 | 410.55 | 432.87 | 455 | 476.89 | 498.54 | 519.94 | 541.14 | 562.11 | 582.71 | 602.97 | 622.92 | 642.61
| Neutral NSW1 | 260.42 | 321.9 | 381.15 | 438.98 | 495.44 | 549.61 | 601.2 | 651.07 | 699.62 | 747.39 | 767.33 | 777.83 | 788.82 | 800.4 | 812.65 | 825.01 | 837.45 | 849.98 | 862.57 | 875.21 | 887.9 | 900.58 | 913.26 | 925.91 | 938.58 | 951.23 | 963.76 | 976.16 | 988.47 | 1000.71
| Neutral QLD2 | 266.28 | 355.72 | 439.98 | 520.48 | 597.97 | 671.71 | 747.57 | 826.82 | 909.74 | 996.02 | 1085.79 | 1177.79 | 1272.98 | 1371.55 | 1474.67 | 1579.08 | 1684.88 | 1792.02 | 1900.51 | 2010.06 | 2120.55 | 2231.83 | 2343.8 | 2456.4 | 2569.94 | 2684.15 | 2798.34 | 2912.61 | 3026.99 | 3141.62
| Neutral SA | 80.28 | 106.23 | 129.82 | 151.98 | 173.67 | 194.76 | 215.56 | 237.03 | 258.84 | 280.54 | 287.58 | 302.21 | 317.27 | 332.85 | 349.04 | 365.3 | 381.66 | 398.12 | 414.69 | 431.4 | 448.22 | 465.12 | 482.1 | 499.13 | 516.27 | 533.47 | 550.63 | 567.75 | 584.82 | 601.86
| Neutral TAS | 12.13 | 13.77 | 25.94 | 37.44 | 48.73 | 58.15 | 67.49 | 78.7 | 90.25 | 101.94 | 100.92 | 99.91 | 98.91 | 97.92 | 96.94 | 95.97 | 95.01 | 94.06 | 93.12 | 92.19 | 91.27 | 91.92 | 92.61 | 93.33 | 105.18 | 117.25 | 129.46 | 141.83 | 154.31 | 166.86
| Neutral VIC | 94.91 | 98.16 | 111.95 | 125.04 | 137.95 | 150.43 | 163.49 | 177.86 | 193.34 | 209.62 | 226.84 | 244.66 | 263.1 | 282.14 | 302.01 | 322.07 | 342.37 | 362.9 | 383.68 | 404.72 | 426.02 | 447.53 | 469.23 | 491.13 | 513.27 | 535.6 | 557.99 | 580.47 | 603.01 | 625.64
| Weak NSW1 | 247.08 | 298.7 | 348.54 | 397.3 | 445.22 | 491.72 | 536.26 | 579.13 | 619.01 | 658.36 | 660.55 | 663.14 | 665.91 | 659.25 | 652.66 | 646.13 | 647.7 | 649.37 | 661.61 | 674.05 | 686.72 | 699.62 | 712.78 | 726.23 | 739.99 | 754.09 | 768.55 | 783.42 | 798.74 | 814.53
| Weak QLD2 | 242.58 | 313.63 | 379.43 | 442.85 | 503.4 | 549.99 | 609.47 | 672.58 | 738.51 | 808.81 | 885.91 | 968.86 | 1053.98 | 1139.89 | 1226.19 | 1310.69 | 1393.32 | 1476.33 | 1560.34 | 1646.62 | 1735.3 | 1826.55 | 1920.54 | 2017.45 | 2117.5 | 2220.92 | 2327.95 | 2438.88 | 2553.81 | 2672.85
| Weak SA | 73.37 | 81.23 | 99.27 | 116.32 | 133.12 | 149.08 | 157 | 164.68 | 163.03 | 161.4 | 159.79 | 158.19 | 156.61 | 155.04 | 153.49 | 151.96 | 150.44 | 148.93 | 154.89 | 161.1 | 178.75 | 197.05 | 216.04 | 235.77 | 256.27 | 277.61 | 299.83 | 323.02 | 347.11 | 372.06
| Weak TAS | 9.5 | 9.41 | 9.31 | 9.22 | 9.13 | 9.04 | 8.95 | 8.86 | 8.77 | 8.68 | 8.6 | 8.51 | 8.42 | 8.34 | 8.26 | 8.17 | 8.09 | 8.01 | 7.93 | 7.85 | 7.77 | 9.28 | 10.89 | 12.61 | 27.29 | 42.89 | 59.5 | 77.18 | 95.85 | 115.38
| Weak VIC | 93.37 | 96.14 | 95.18 | 103.8 | 112.16 | 120.51 | 119.31 | 121.94 | 124.73 | 139.67 | 155.26 | 171.55 | 188.05 | 204.77 | 221.66 | 238.77 | 256.17 | 273.92 | 292.09 | 310.75 | 329.94 | 349.67 | 370 | 390.96 | 412.6 | 434.96 | 458.11 | 482.09 | 506.94 | 532.65
1. For the modelling process, the capacity from explicitly modelled small non-scheduled PV generators is then netted off the AEMO 2018 ESOO forecast. For NSW this includes Griffith Solar Farm.
2. For the modelling process, the capacity from explicitly modelled small non-scheduled PV generators is then netted off the AEMO 2018 ESOO forecast. For QLD this includes Hughenden Solar Farm and Longreach Solar Farm.

## Small non-scheduled hydro
TOC
Small non-scheduled Tasmanian hydro generation (GWh)
Primary source: NEM-Review
The inflow for small non-scheduled Tasmanian hydro generators is encapsulated within the 10 pond Tasmanian hydro scheme. There their generation (based on the 8 reference year cylce) is added back to demand.
| Generation (GWh) | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Historical profile | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
| Small non-scheduled Tasmanian hydro generation (GWh) | 513.6928 | 492.9787 | 400.331 | 476.3894 | 416.308 | 434.4491 | 430.4544 | 507.3197 | 515.7496 | 490.2726 | 400.995 | 476.9196 | 416.7349 | 433.3766 | 431.2289 | 508.7425 | 513.6035 | 487.2908 | 399.8752 | 478.2827 | 416.4697 | 432.2867 | 431.3726 | 506.1954 | 514.597 | 490.8822 | 401.6789 | 476.6829 | 416.1979 | 434.0344

## Battery storage
TOC
Behind-the-meter storage uptake (MW and MWh)
| Primary source: AEMO Electricity Statement of Opportunities 2018 | AEMO's forecasting data portal
| Stong: | To be used in Accelerated Transition to a Low Emissions Future scenario
| Neutral: | To be used in Status Quo scenario and Sustained Renewables Uptake scenario
| Weak: | To be used in Global Slowdown scenario
| Scenario and Region | AEMO forecast
| Capacity (MW) | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Historical profile | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
| Stong NSW | 175.95 | 210.32 | 266.41 | 351.18 | 435.63 | 491.1 | 501.05 | 524.62 | 580.78 | 755.92 | 923.92 | 1153.01 | 1390.48 | 1634.68 | 1782.18 | 1861.09 | 1953.86 | 2062.45 | 2187.72 | 2346.43 | 2511.13 | 2683.79 | 2864.74 | 3054.2 | 3256.66 | 3465.26 | 3675.53 | 3897.5 | 4111.26 | 4317.1
| Stong QLD | 71.32 | 85.18 | 107.41 | 148.05 | 186.85 | 218.51 | 223.72 | 242.87 | 283.82 | 376.63 | 450.1 | 571.5 | 691.73 | 790.89 | 846.44 | 882 | 922.53 | 968.79 | 1021.16 | 1085.07 | 1152.06 | 1222.84 | 1297.62 | 1376.61 | 1461.36 | 1549.83 | 1640.71 | 1737.39 | 1833.43 | 1928.98
| Stong SA | 169.81 | 171.21 | 172.82 | 175.21 | 178.24 | 180.52 | 182.01 | 184.4 | 187.02 | 206.9 | 248.37 | 308.21 | 369.88 | 426.88 | 460.87 | 482.27 | 507.1 | 535.8 | 567.24 | 604.46 | 642.74 | 682.5 | 723.82 | 766.7 | 812.25 | 858.7 | 904.9 | 953.33 | 999.4 | 1043.22
| Stong TAS | 12.8 | 14.75 | 17.92 | 22.93 | 28.47 | 31.77 | 32.28 | 33.81 | 37.69 | 49.58 | 61.64 | 78.07 | 96.21 | 113.71 | 124.49 | 131.05 | 138.78 | 146.21 | 154.82 | 165.84 | 177.13 | 188.8 | 200.81 | 213.18 | 226.14 | 239.25 | 252.23 | 265.65 | 277.82 | 288.78
| Stong VIC | 80.91 | 96.58 | 125.35 | 175.76 | 239.98 | 277.13 | 283.39 | 301.58 | 341.85 | 452.31 | 575.28 | 749.04 | 932.86 | 1110.4 | 1218.37 | 1282.03 | 1353.9 | 1435.27 | 1524.41 | 1633.22 | 1746.47 | 1865.72 | 1991.31 | 2123.45 | 2265.78 | 2412.89 | 2561.18 | 2718.78 | 2874.5 | 3028.86
| Neutral NSW | 173.08 | 188.9 | 217.27 | 265.19 | 317.37 | 343.03 | 358.91 | 386.92 | 418.19 | 465.33 | 503.45 | 561.19 | 631.5 | 711.63 | 796.67 | 866.26 | 939.04 | 1015.4 | 1095.38 | 1179.63 | 1266.9 | 1358.36 | 1454.2 | 1554.46 | 1662 | 1772.33 | 1882.37 | 1998.59 | 2121.04 | 2250.83
| Neutral QLD | 66.53 | 71.6 | 80.46 | 98.67 | 120 | 131.54 | 141.76 | 158.91 | 178.04 | 202.49 | 224.26 | 256.44 | 295.2 | 338.28 | 386.99 | 429.03 | 474.52 | 523.92 | 577.53 | 633.32 | 692.44 | 755.75 | 823.46 | 895.82 | 974.82 | 1057.75 | 1142.64 | 1233.95 | 1330.9 | 1434.33
| Neutral SA | 169.47 | 170.52 | 171.68 | 173.02 | 174.4 | 175.6 | 177.14 | 179.34 | 181.44 | 183.45 | 185.58 | 188.25 | 195.45 | 210.17 | 231.88 | 250.97 | 271.17 | 292.6 | 315.28 | 339.43 | 364.36 | 390.39 | 417.56 | 445.84 | 476.02 | 506.83 | 537.42 | 569.54 | 602.66 | 636.96
| Neutral TAS | 13.42 | 14.3 | 15.92 | 18.65 | 21.74 | 23.71 | 25.58 | 29.01 | 32.81 | 37.22 | 41.01 | 46 | 51.3 | 56.75 | 62.56 | 67.29 | 72.33 | 77.72 | 83.5 | 89.72 | 96.1 | 102.72 | 109.57 | 116.66 | 124.15 | 131.74 | 139.22 | 146.98 | 154.78 | 162.61
| Neutral VIC | 82.96 | 90.25 | 103.36 | 125.77 | 155.02 | 172.19 | 185.72 | 214.04 | 244.17 | 279.82 | 313.73 | 359.88 | 411.76 | 469.07 | 532.1 | 585.15 | 642.01 | 703.23 | 769.11 | 840.37 | 915.32 | 994.96 | 1079.51 | 1169.11 | 1266.23 | 1367.24 | 1469.55 | 1578.7 | 1693.24 | 1814.05
| Weak NSW | 77.29 | 86.73 | 104.53 | 129.55 | 156.4 | 172.11 | 177 | 179.69 | 182.44 | 192.84 | 210.38 | 226.53 | 248.8 | 282.62 | 306.25 | 324.81 | 344.22 | 364.51 | 385.91 | 408.36 | 431.57 | 455.43 | 480.14 | 505.76 | 533.12 | 561.08 | 588.49 | 617.29 | 647.37 | 679.03
| Weak QLD | 28.37 | 31.23 | 36.55 | 44.03 | 52.13 | 57.04 | 58.79 | 61.78 | 64.8 | 71.72 | 84.23 | 95.89 | 108.46 | 122.55 | 133.14 | 139.99 | 147.2 | 154.75 | 162.74 | 171.15 | 182.37 | 196.95 | 212.54 | 229.23 | 247.49 | 266.83 | 286.63 | 308.01 | 330.03 | 352.74
| Weak SA | 166.96 | 167.89 | 168.87 | 169.92 | 170.98 | 171.95 | 172.87 | 173.79 | 174.72 | 175.64 | 176.84 | 178.28 | 179.86 | 181.56 | 183.04 | 184.39 | 185.82 | 187.34 | 188.93 | 190.64 | 192.43 | 195.04 | 200.73 | 209.17 | 219.34 | 230.75 | 242.6 | 255.25 | 267.39 | 278.95
| Weak TAS | 6 | 6.57 | 7.65 | 9.16 | 10.73 | 11.61 | 11.82 | 11.92 | 12.01 | 12.52 | 13.77 | 15.58 | 18.29 | 21.74 | 24.2 | 26.24 | 28.59 | 30.74 | 33.2 | 36.23 | 39.47 | 42.92 | 46.59 | 50.49 | 54.67 | 59.03 | 63.46 | 68.13 | 72.45 | 76.4
| Weak VIC | 35.48 | 39.51 | 47.25 | 59.46 | 73.69 | 85.03 | 90.21 | 96.16 | 100.87 | 111.11 | 121.96 | 132.49 | 146.59 | 167.11 | 182.82 | 195.84 | 210.11 | 225.76 | 243.13 | 262.31 | 282.59 | 303.93 | 326.49 | 350.35 | 376.2 | 403.21 | 430.48 | 459.56 | 489.2 | 519.49
| Scenario and Region | AEMO forecast 2020-21 2011-12: AEMO forecast
| Capacity (MWh) | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Historical profile | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
| Stong NSW | 457.46 | 546.83 | 692.67 | 913.07 | 1132.65 | 1276.86 | 1302.73 | 1364 | 1510.02 | 1965.39 | 2402.2 | 2997.83 | 3615.23 | 4250.17 | 4633.66 | 4838.83 | 5080.03 | 5362.37 | 5688.05 | 6100.71 | 6528.94 | 6977.86 | 7448.33 | 7940.94 | 8467.31 | 9009.67 | 9556.37 | 10133.5 | 10689.28 | 11224.47
| Stong QLD | 185.43 | 221.48 | 279.27 | 384.93 | 485.8 | 568.11 | 581.68 | 631.46 | 737.94 | 979.24 | 1170.26 | 1485.9 | 1798.49 | 2056.31 | 2200.75 | 2293.19 | 2398.59 | 2518.85 | 2655 | 2821.18 | 2995.35 | 3179.38 | 3373.82 | 3579.19 | 3799.52 | 4029.55 | 4265.85 | 4517.22 | 4766.92 | 5015.35
| Stong SA | 441.48 | 445.14 | 449.32 | 455.54 | 463.42 | 469.36 | 473.21 | 479.45 | 486.24 | 537.94 | 645.75 | 801.34 | 961.7 | 1109.88 | 1198.25 | 1253.9 | 1318.46 | 1393.09 | 1474.81 | 1571.61 | 1671.1 | 1774.49 | 1881.92 | 1993.44 | 2111.86 | 2232.62 | 2352.76 | 2478.68 | 2598.44 | 2712.36
| Stong TAS | 33.27 | 38.35 | 46.58 | 59.63 | 74.02 | 82.61 | 83.92 | 87.89 | 97.98 | 128.91 | 160.25 | 202.98 | 250.16 | 295.66 | 323.68 | 340.73 | 360.83 | 380.15 | 402.53 | 431.19 | 460.55 | 490.86 | 522.11 | 554.27 | 587.96 | 622.04 | 655.79 | 690.68 | 722.32 | 750.83
| Stong VIC | 210.35 | 251.1 | 325.91 | 456.99 | 623.95 | 720.53 | 736.82 | 784.1 | 888.83 | 1176 | 1495.73 | 1947.5 | 2425.44 | 2887.03 | 3167.77 | 3333.29 | 3520.12 | 3731.7 | 3963.45 | 4246.36 | 4540.82 | 4850.89 | 5177.42 | 5520.98 | 5891.03 | 6273.51 | 6659.07 | 7068.83 | 7473.68 | 7875.05
| Neutral NSW | 450.01 | 491.15 | 564.9 | 689.51 | 825.17 | 891.89 | 933.17 | 1006 | 1087.31 | 1209.85 | 1308.97 | 1459.09 | 1641.9 | 1850.24 | 2071.32 | 2252.27 | 2441.51 | 2640.04 | 2847.99 | 3067.04 | 3293.94 | 3531.76 | 3780.91 | 4041.59 | 4321.2 | 4608.06 | 4894.16 | 5196.35 | 5514.72 | 5852.15
| Neutral QLD | 172.98 | 186.15 | 209.21 | 256.55 | 312.01 | 342.01 | 368.57 | 413.16 | 462.92 | 526.48 | 583.06 | 666.76 | 767.52 | 879.52 | 1006.16 | 1115.48 | 1233.77 | 1362.2 | 1501.58 | 1646.63 | 1800.36 | 1964.94 | 2141.01 | 2329.11 | 2534.53 | 2750.14 | 2970.84 | 3208.27 | 3460.33 | 3729.25
| Neutral SA | 440.61 | 443.34 | 446.36 | 449.85 | 453.44 | 456.58 | 460.57 | 466.29 | 471.74 | 476.98 | 482.52 | 489.45 | 508.18 | 546.45 | 602.87 | 652.51 | 705.06 | 760.76 | 819.71 | 882.51 | 947.35 | 1015.03 | 1085.64 | 1159.18 | 1237.65 | 1317.77 | 1397.3 | 1480.82 | 1566.9 | 1656.11
| Neutral TAS | 34.9 | 37.2 | 41.4 | 48.49 | 56.52 | 61.62 | 66.52 | 75.43 | 85.31 | 96.77 | 106.64 | 119.61 | 133.35 | 147.53 | 162.64 | 174.94 | 188.04 | 202.08 | 217.1 | 233.27 | 249.86 | 267.08 | 284.9 | 303.32 | 322.8 | 342.52 | 361.96 | 382.17 | 402.42 | 422.79
| Neutral VIC | 215.69 | 234.65 | 268.74 | 326.99 | 403.04 | 447.7 | 482.87 | 556.5 | 634.84 | 727.54 | 815.68 | 935.68 | 1070.58 | 1219.58 | 1383.48 | 1521.37 | 1669.23 | 1828.42 | 1999.69 | 2184.97 | 2379.84 | 2586.9 | 2806.73 | 3039.7 | 3292.21 | 3554.82 | 3820.83 | 4104.61 | 4402.42 | 4716.53
| Weak NSW | 200.96 | 225.5 | 271.76 | 336.83 | 406.62 | 447.49 | 460.21 | 467.2 | 474.32 | 501.39 | 546.99 | 588.96 | 646.89 | 734.83 | 796.25 | 844.52 | 894.99 | 947.71 | 1003.38 | 1061.72 | 1122.09 | 1184.14 | 1248.37 | 1314.98 | 1386.11 | 1458.79 | 1530.07 | 1604.94 | 1683.15 | 1765.49
| Weak QLD | 73.76 | 81.2 | 95.04 | 114.49 | 135.55 | 148.28 | 152.84 | 160.62 | 168.47 | 186.46 | 218.99 | 249.31 | 282.01 | 318.63 | 346.16 | 363.99 | 382.71 | 402.34 | 423.13 | 445 | 474.17 | 512.09 | 552.61 | 596 | 643.49 | 693.74 | 745.26 | 800.83 | 858.08 | 917.13
| Weak SA | 434.1 | 436.51 | 439.06 | 441.78 | 444.53 | 447.09 | 449.46 | 451.85 | 454.25 | 456.67 | 459.76 | 463.52 | 467.64 | 472.08 | 475.89 | 479.41 | 483.13 | 487.09 | 491.22 | 495.66 | 500.3 | 507.1 | 521.89 | 543.83 | 570.3 | 599.93 | 630.77 | 663.65 | 695.21 | 725.25
| Weak TAS | 15.6 | 17.06 | 19.88 | 23.81 | 27.92 | 30.19 | 30.75 | 31 | 31.25 | 32.54 | 35.81 | 40.51 | 47.56 | 56.54 | 62.92 | 68.21 | 74.34 | 79.92 | 86.32 | 94.18 | 102.63 | 111.6 | 121.14 | 131.26 | 142.15 | 153.47 | 165.01 | 177.13 | 188.36 | 198.62
| Weak VIC | 92.27 | 102.74 | 122.83 | 154.61 | 191.61 | 221.07 | 234.54 | 250.03 | 262.27 | 288.9 | 317.08 | 344.49 | 381.11 | 434.48 | 475.34 | 509.19 | 546.28 | 586.99 | 632.14 | 681.99 | 734.74 | 790.21 | 848.87 | 910.92 | 978.13 | 1048.34 | 1119.26 | 1194.85 | 1271.92 | 1350.68

## Electric Vehicles
TOC
Electric vehicles demand projections (GWh)
| Primary source: AEMO Electricity Statement of Opportunities 2018 | AEMO's forecasting data portal
| Stong: | To be used in Accelerated Transition to a Low Emissions Future scenario
| Neutral: | To be used in Status Quo scenario and Sustained Renewables Uptake scenario
| Weak: | To be used in Global Slowdown scenario
| Scenario and Region | [18 empty] | Extrapolated
| EV demand (GWh) | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Historical profile | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
| Stong NSW | 57.9491 | 111.0175 | 205.8779 | 369.9463 | 646.363 | 1015.2208 | 1526.2825 | 2236.9486 | 3082.2657 | 3907.3872 | 4718.251 | 5512.7735 | 6306.1171 | 7106.2903 | 7876.6231 | 8744.6066 | 9628.5155 | 10515.2381 | 11456.9998 | 12491.8962 | 12590.2499 | 12724 | 12855.9999 | 13024.0979 | 13119.9999 | 13250.1586 | 13383.1399 | 13554.568 | 13649.0001 | 13780.9998
| Stong QLD | 27.3431 | 58.7093 | 116.6039 | 217.5418 | 389.7297 | 619.3168 | 940.9319 | 1394.6424 | 1908.1441 | 2419.2476 | 2933.1568 | 3449.3622 | 3981.6579 | 4536.3543 | 5091.2019 | 5726.9915 | 6390.1843 | 7072.1356 | 7802 | 8604.6595 | 9414.6916 | 9558.9998 | 9701.9998 | 9872.3624 | 9988.0001 | 10129.5924 | 10272.5721 | 10445.9521 | 10560 | 10703.0002
| Stong SA | 9.5503 | 19.9925 | 39.1288 | 71.9562 | 125.4167 | 195.8989 | 291.8163 | 422.1131 | 567.5193 | 709.1648 | 848.0451 | 982.3922 | 1117.7316 | 1254.5871 | 1388.0438 | 1540.027 | 1697.3849 | 1858.303 | 2041 | 2234.8854 | 2428.6625 | 2641 | 2664 | 2695.4709 | 2711 | 2733.6201 | 2756.6169 | 2788.7293 | 2804 | 2827
| Stong TAS | 2.9108 | 5.9677 | 11.2749 | 20.0814 | 34.2675 | 53.0126 | 77.6806 | 110.0753 | 141.5012 | 170.8896 | 199.1617 | 226.0551 | 253.6468 | 282.9867 | 312.8008 | 346.9799 | 383.8665 | 422.4141 | 462 | 506.3334 | 549.9236 | 598 | 649 | 704.9539 | 760 | 764.8937 | 769.893 | 777.154 | 781 | 786
| Stong VIC | 65.801 | 124.0223 | 226.1743 | 393.9166 | 659.6396 | 1007.5801 | 1480.9113 | 2126.6288 | 2878.1857 | 3625.0068 | 4369.2324 | 5104.0297 | 5843.8039 | 6592.729 | 7315.9328 | 8124.1341 | 8943.7852 | 9767.3104 | 10644.9998 | 10822.5 | 10940.4793 | 11091.0001 | 11239.9999 | 11419.6511 | 11536.9999 | 11684.3761 | 11833.3552 | 12016.3047 | 12131.9999 | 12281.0001
| Neutral NSW | 31.6887 | 52.6427 | 88.0367 | 146.6134 | 234.7173 | 370.6866 | 574.6277 | 873.3025 | 1305.1699 | 1901.6574 | 2507.88 | 3105.0389 | 3698.445 | 4289.7801 | 4850.6955 | 5460.952 | 6072.7503 | 6681.2531 | 7327 | 8035.1603 | 8742.7854 | 9519.0003 | 10341.0006 | 11246.1696 | 12141.9998 | 13123.1755 | 13241.1595 | 13398.1349 | 13478.0006 | 13596
| Neutral QLD | 13.4985 | 26.2845 | 47.5689 | 82.3575 | 134.952 | 216.4324 | 339.7941 | 520.5461 | 778.2184 | 1128.2187 | 1484.0029 | 1841.9122 | 2204.944 | 2577.1701 | 2940.929 | 3341.7434 | 3750.2612 | 4162.6433 | 4603.9998 | 5088.4005 | 5577.2248 | 6113.9997 | 6685.0002 | 7314.2718 | 7942.0001 | 8631.8003 | 9366.6985 | 9508.3532 | 9595.0003 | 9709.0004
| Neutral SA | 4.682 | 8.5747 | 15.2411 | 26.1475 | 42.2471 | 66.7669 | 102.9348 | 154.929 | 228.6437 | 325.5844 | 421.6564 | 516.315 | 610.8896 | 706.704 | 798.3406 | 899.2214 | 1002.1924 | 1104.7296 | 1227 | 1353.5645 | 1480.7942 | 1619 | 1764.9999 | 1925.3363 | 2085 | 2258.6861 | 2442.6605 | 2646.3345 | 2656.9999 | 2675.0001
| Neutral TAS | 1.3562 | 2.3285 | 4.0471 | 6.7814 | 10.5985 | 16.4309 | 24.7098 | 35.8162 | 49.7569 | 66.8137 | 83.1544 | 98.9922 | 115.3777 | 133.108 | 150.7751 | 171.1312 | 192.6107 | 214.5656 | 238 | 263.6944 | 288.9598 | 316 | 345 | 376.0422 | 407 | 440.9387 | 476.9338 | 516.4314 | 554 | 596
| Neutral VIC | 33.1085 | 53.7107 | 88.7077 | 146.4625 | 231.3958 | 360.4487 | 552.0909 | 831.7979 | 1230.1907 | 1764.3581 | 2308.5474 | 2850.406 | 3391.9283 | 3933.6048 | 4447.3165 | 5002.2453 | 5553.3946 | 6095.7683 | 6674.9996 | 7310.2511 | 7945.8954 | 8644.9997 | 9386.9996 | 10205.2854 | 10292.0005 | 10405.5537 | 10520.5385 | 10665.5602 | 10751.0001 | 10866.0004
| Weak NSW | 14.589 | 20.3621 | 30.9921 | 48.7047 | 71.9966 | 107.2234 | 156.8355 | 228.0575 | 328.5719 | 467.6632 | 690.5776 | 970.925 | 1325.0464 | 1763.5298 | 2289.0673 | 2839.416 | 3395.244 | 3954.8869 | 4551 | 5198.6902 | 5858.1859 | 6576 | 7338.0001 | 8169.6432 | 9007.0002 | 9917.6215 | 10885.4873 | 11948.1154 | 13005.0001 | 13109.0002
| Weak QLD | 3.8239 | 7.2082 | 14.001 | 25.5976 | 41.2528 | 64.4421 | 97.4355 | 144.4119 | 209.9435 | 299.2325 | 428.4324 | 591.3883 | 799.3526 | 1063.2221 | 1386.1883 | 1728.8327 | 2079.9948 | 2435.8258 | 2816 | 3230.5072 | 3654.4921 | 4117 | 4609.9999 | 5148.2691 | 5693.0001 | 6287.1261 | 6919.0384 | 7614.1034 | 8309 | 8392.0001
| Weak SA | 1.8387 | 2.9095 | 5.0949 | 9.1831 | 14.6927 | 22.7879 | 34.5205 | 50.8048 | 73.1722 | 102.8389 | 147.904 | 200.389 | 262.7254 | 338.3929 | 428.4247 | 524.1137 | 621.0028 | 716.7674 | 833 | 951.5057 | 1070.8512 | 1201 | 1338 | 1488.1245 | 1638 | 1800.7497 | 1973.7257 | 2162.995 | 2350 | 2554
| Weak TAS | 0.88778 | 0.99264 | 1.3667 | 2.2699 | 3.4061 | 5.2268 | 7.5885 | 10.7942 | 14.9487 | 20.1909 | 26.845 | 34.6372 | 44.3581 | 56.9068 | 72.5448 | 89.5652 | 107.2371 | 125.2255 | 144 | 164.433 | 184.9743 | 207 | 230 | 254.7059 | 279 | 305.9575 | 333.9536 | 364.0089 | 394 | 427
| Weak VIC | 15.5406 | 21.3072 | 32.1246 | 50.3608 | 75.0005 | 111.3411 | 162.222 | 234.009 | 333.8851 | 471.1726 | 715.2551 | 1007.4538 | 1356.3551 | 1768.0067 | 2239.4786 | 2731.0625 | 3223.6755 | 3713.4494 | 4234.0001 | 4802.6473 | 5380.2522 | 6011.0001 | 6680 | 7413.5474 | 8149.9999 | 8954.7555 | 9809.6367 | 9929.5208 | 9992.9999 | 10083.0002

## DSP
TOC
Demand-side participation (MW)
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
| Stong: | To be used in Accelerated Transition to a Low Emissions Future scenario
| Neutral: | To be used in Status Quo scenario and Sustained Renewables Uptake scenario
| Weak: | To be used in Global Slowdown scenario
Neutral
Queensland
| Summer | AEMO Feb 2019 ISP forecast | [20 empty] | AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 35.0223 | 37.4238 | 38.8108 | 40.3889 | 42.3314 | 43.1421 | 45.3484 | 48.2758 | 50.3232 | 51.5702 | 53.0035 | 53.8757 | 55.23 | 57.875 | 59.6883 | 61.6696 | 63.3588 | 63.0905 | 64.9843 | 66.8961 | 66.8961 | 72.7399 | 74.7239 | 76.726 | 78.7461 | 80.7842 | 82.8404 | 84.9147 | 87.007 | 89.1173
| $500 - $1,000 | 0.38842 | 0.41505 | 0.43043 | 0.44794 | 0.46948 | 0.47847 | 0.50294 | 0.53541 | 0.55811 | 0.57194 | 0.58784 | 0.59751 | 0.61253 | 0.64187 | 0.66198 | 0.68395 | 0.70269 | 0.69971 | 0.72071 | 0.74192 | 0.74192 | 0.80673 | 0.82873 | 0.85093 | 0.87334 | 0.89594 | 0.91875 | 0.94175 | 0.96496 | 0.98836
| $1,000 - $7,500 | 1.176 | 1.2567 | 1.3033 | 1.3563 | 1.4215 | 1.4487 | 1.5228 | 1.6211 | 1.6898 | 1.7317 | 1.7798 | 1.8091 | 1.8546 | 1.9434 | 2.0043 | 2.0709 | 2.1276 | 2.1186 | 2.1822 | 2.2464 | 2.2464 | 2.4426 | 2.5092 | 2.5764 | 2.6443 | 2.7127 | 2.7818 | 2.8514 | 2.9217 | 2.9925
| $7,500 - MPC | 6.8944 | 7.3672 | 7.6402 | 7.9509 | 8.3333 | 8.4929 | 8.9272 | 9.5035 | 9.9065 | 10.152 | 10.4342 | 10.6059 | 10.8724 | 11.3931 | 11.7501 | 12.1401 | 12.4727 | 12.4198 | 12.7927 | 13.169 | 13.169 | 14.3194 | 14.71 | 15.1041 | 15.5018 | 15.903 | 16.3078 | 16.7161 | 17.128 | 17.5434
| MPC | 189.9683 | 202.9947 | 210.5183 | 219.0782 | 229.6145 | 234.0121 | 245.9797 | 261.858 | 272.9639 | 279.728 | 287.5026 | 292.2335 | 299.5793 | 313.9262 | 323.7621 | 334.5094 | 343.6718 | 342.2164 | 352.4887 | 362.8588 | 362.8588 | 394.5567 | 405.3184 | 416.178 | 427.1355 | 438.1909 | 449.3442 | 460.5954 | 471.9444 | 483.3914
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 35.6642 | 37.5711 | 39.4311 | 41.0965 | 42.5687 | 44.3402 | 47.1498 | 49.1788 | 50.8992 | 52.2082 | 54.2172 | 56.2999 | 58.3806 | 60.1988 | 61.6958 | 63.0391 | 65.8321 | 67.0766 | 69.0425 | 71.0277 | 71.0277 | 77.0987 | 79.1609 | 81.2424 | 83.3431 | 85.463 | 87.6022 | 89.7607 | 91.9384 | 94.1353
| $500 - $1,000 | 0.39554 | 0.41669 | 0.43731 | 0.45578 | 0.47211 | 0.49176 | 0.52292 | 0.54542 | 0.5645 | 0.57902 | 0.6013 | 0.6244 | 0.64747 | 0.66764 | 0.68424 | 0.69914 | 0.73012 | 0.74392 | 0.76572 | 0.78774 | 0.78774 | 0.85507 | 0.87794 | 0.90102 | 0.92432 | 0.94783 | 0.97156 | 0.9955 | 1.0196 | 1.044
| $1,000 - $7,500 | 1.1976 | 1.2616 | 1.3241 | 1.38 | 1.4294 | 1.4889 | 1.5833 | 1.6514 | 1.7092 | 1.7531 | 1.8206 | 1.8905 | 1.9604 | 2.0215 | 2.0717 | 2.1168 | 2.2106 | 2.2524 | 2.3184 | 2.3851 | 2.3851 | 2.589 | 2.6582 | 2.7281 | 2.7986 | 2.8698 | 2.9417 | 3.0141 | 3.0873 | 3.161
| $7,500 - MPC | 7.0208 | 7.3962 | 7.7623 | 8.0902 | 8.38 | 8.7287 | 9.2818 | 9.6812 | 10.0199 | 10.2776 | 10.6731 | 11.0831 | 11.4927 | 11.8506 | 12.1453 | 12.4097 | 12.9596 | 13.2045 | 13.5915 | 13.9823 | 13.9823 | 15.1775 | 15.5834 | 15.9932 | 16.4067 | 16.8241 | 17.2452 | 17.6701 | 18.0988 | 18.5313
| MPC | 171.4761 | 180.6447 | 189.5878 | 197.5948 | 204.6733 | 213.1909 | 226.6995 | 236.455 | 244.727 | 251.0206 | 260.6801 | 270.6941 | 280.6981 | 289.4399 | 296.638 | 303.0966 | 316.5254 | 322.5089 | 331.9612 | 341.5062 | 341.5062 | 370.6963 | 380.6115 | 390.6192 | 400.7195 | 410.9123 | 421.1978 | 431.5757 | 442.0463 | 452.6094
New South Wales
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 108.0428 | 124.3374 | 139.6579 | 155.3028 | 170.6709 | 189.0836 | 208.1586 | 227.304 | 242.2635 | 257.6907 | 278.0438 | 292.7794 | 309.5983 | 328.5481 | 345.6494 | 363.7884 | 389.4479 | 404.0981 | 423.5158 | 443.1456 | 443.1456 | 503.3073 | 523.7854 | 544.4756 | 565.3778 | 586.4921 | 607.8185 | 629.357 | 651.1075 | 673.0702
| $500 - $1,000 | 0.37529 | 0.43189 | 0.48511 | 0.53945 | 0.59284 | 0.65679 | 0.72305 | 0.78955 | 0.84152 | 0.8951 | 0.9658 | 1.017 | 1.0754 | 1.1412 | 1.2006 | 1.2636 | 1.3528 | 1.4037 | 1.4711 | 1.5393 | 1.5393 | 1.7483 | 1.8194 | 1.8913 | 1.9639 | 2.0372 | 2.1113 | 2.1861 | 2.2617 | 2.338
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 37.5432 | 43.2054 | 48.529 | 53.9654 | 59.3056 | 65.7037 | 72.332 | 78.9847 | 84.1829 | 89.5436 | 96.616 | 101.7364 | 107.5807 | 114.1655 | 120.1079 | 126.411 | 135.3273 | 140.418 | 147.1653 | 153.9864 | 153.9864 | 174.8917 | 182.0075 | 189.197 | 196.4602 | 203.7971 | 211.2077 | 218.692 | 226.25 | 233.8817
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 106.5544 | 121.6801 | 137.0607 | 153.3086 | 167.8506 | 185.994 | 204.6604 | 222.6753 | 240.9582 | 255.9211 | 273.4598 | 293.9347 | 312.0123 | 332.788 | 355.1466 | 371.3282 | 397.058 | 414.3212 | 435.5603 | 457.1417 | 457.1417 | 523.9398 | 546.8905 | 570.1835 | 593.8188 | 617.7964 | 642.1164 | 666.7787 | 691.7833 | 717.1302
| $500 - $1,000 | 0.37012 | 0.42266 | 0.47609 | 0.53253 | 0.58304 | 0.64606 | 0.7109 | 0.77348 | 0.83698 | 0.88896 | 0.94988 | 1.021 | 1.0838 | 1.156 | 1.2336 | 1.2898 | 1.3792 | 1.4392 | 1.5129 | 1.5879 | 1.5879 | 1.8199 | 1.8997 | 1.9806 | 2.0627 | 2.146 | 2.2304 | 2.3161 | 2.403 | 2.491
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 37.0261 | 42.282 | 47.6265 | 53.2724 | 58.3256 | 64.6301 | 71.1164 | 77.3763 | 83.7293 | 88.9287 | 95.0231 | 102.1379 | 108.4195 | 115.6388 | 123.4081 | 129.031 | 137.9716 | 143.9703 | 151.3506 | 158.8498 | 158.8498 | 182.0612 | 190.0362 | 198.1301 | 206.3431 | 214.6749 | 223.1257 | 231.6955 | 240.3842 | 249.1919
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victoria
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 38.1748 | 43.9435 | 47.927 | 51.5418 | 57.3114 | 62.2751 | 67.5559 | 73.2614 | 78.4449 | 84.3275 | 89.0691 | 95.2638 | 101.2641 | 105.7532 | 109.7958 | 117.4408 | 124.6182 | 128.8018 | 134.6841 | 140.6145 | 140.6145 | 158.6939 | 164.8165 | 170.9872 | 177.2059 | 183.4726 | 189.7874 | 196.1503 | 202.5612 | 209.0202
| $500 - $1,000 | 4.0896 | 4.7075 | 5.1343 | 5.5215 | 6.1396 | 6.6714 | 7.2371 | 7.8483 | 8.4036 | 9.0338 | 9.5417 | 10.2053 | 10.8481 | 11.329 | 11.7621 | 12.5811 | 13.35 | 13.7982 | 14.4283 | 15.0636 | 15.0636 | 17.0004 | 17.6563 | 18.3174 | 18.9836 | 19.6549 | 20.3314 | 21.013 | 21.6998 | 22.3918
| $1,000 - $7,500 | 2.1524 | 2.4777 | 2.7023 | 2.9061 | 3.2314 | 3.5112 | 3.809 | 4.1307 | 4.4229 | 4.7546 | 5.022 | 5.3712 | 5.7095 | 5.9627 | 6.1906 | 6.6216 | 7.0263 | 7.2622 | 7.5939 | 7.9282 | 7.9282 | 8.9476 | 9.2928 | 9.6407 | 9.9914 | 10.3447 | 10.7007 | 11.0595 | 11.421 | 11.7851
| $7,500 - MPC | 0.88787 | 1.022 | 1.1147 | 1.1988 | 1.3329 | 1.4484 | 1.5712 | 1.7039 | 1.8245 | 1.9613 | 2.0716 | 2.2156 | 2.3552 | 2.4596 | 2.5536 | 2.7314 | 2.8984 | 2.9957 | 3.1325 | 3.2704 | 3.2704 | 3.6909 | 3.8333 | 3.9768 | 4.1214 | 4.2672 | 4.4141 | 4.562 | 4.7111 | 4.8614
| MPC | 58.5184 | 67.3612 | 73.4676 | 79.0087 | 87.8531 | 95.4619 | 103.5568 | 112.3029 | 120.2486 | 129.2661 | 136.5345 | 146.0304 | 155.2283 | 162.1097 | 168.3067 | 180.0256 | 191.028 | 197.4411 | 206.4581 | 215.5488 | 215.5488 | 243.2628 | 252.6482 | 262.1072 | 271.6399 | 281.2462 | 290.9263 | 300.6799 | 310.5073 | 320.4083
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 46.2061 | 55.1565 | 63.3412 | 71.9342 | 80.2684 | 88.2698 | 99.0359 | 108.6035 | 119.0805 | 128.508 | 137.1636 | 149.2975 | 159.8409 | 169.5051 | 180.5924 | 191.5764 | 203.6471 | 216.1936 | 228.4049 | 240.8319 | 240.8319 | 279.4071 | 292.6969 | 306.2024 | 319.9235 | 333.8604 | 348.0129 | 362.3811 | 376.965 | 391.7646
| $500 - $1,000 | 4.9499 | 5.9088 | 6.7856 | 7.7061 | 8.5989 | 9.4561 | 10.6094 | 11.6344 | 12.7568 | 13.7667 | 14.694 | 15.9938 | 17.1233 | 18.1586 | 19.3464 | 20.523 | 21.8161 | 23.1602 | 24.4684 | 25.7997 | 25.7997 | 29.9321 | 31.3558 | 32.8026 | 34.2725 | 35.7655 | 37.2817 | 38.8209 | 40.3832 | 41.9686
| $1,000 - $7,500 | 2.6052 | 3.1099 | 3.5714 | 4.0558 | 4.5258 | 4.9769 | 5.5839 | 6.1234 | 6.7141 | 7.2456 | 7.7337 | 8.4178 | 9.0123 | 9.5572 | 10.1823 | 10.8016 | 11.4822 | 12.1896 | 12.8781 | 13.5788 | 13.5788 | 15.7537 | 16.5031 | 17.2645 | 18.0382 | 18.824 | 19.6219 | 20.432 | 21.2543 | 22.0888
| $7,500 - MPC | 1.0747 | 1.2828 | 1.4732 | 1.673 | 1.8669 | 2.053 | 2.3034 | 2.5259 | 2.7696 | 2.9888 | 3.1901 | 3.4723 | 3.7176 | 3.9423 | 4.2002 | 4.4557 | 4.7364 | 5.0282 | 5.3122 | 5.6012 | 5.6012 | 6.4984 | 6.8075 | 7.1216 | 7.4407 | 7.7649 | 8.094 | 8.4282 | 8.7674 | 9.1116
| MPC | 10.5837 | 12.6339 | 14.5086 | 16.4769 | 18.3859 | 20.2186 | 22.6846 | 24.8762 | 27.276 | 29.4354 | 31.418 | 34.1973 | 36.6123 | 38.826 | 41.3656 | 43.8815 | 46.6464 | 49.5202 | 52.3173 | 55.1637 | 55.1637 | 63.9996 | 67.0437 | 70.1372 | 73.2801 | 76.4724 | 79.7141 | 83.0052 | 86.3457 | 89.7356
South Australia
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 3.1942 | 4.1003 | 5.0211 | 6.0119 | 6.8831 | 7.9672 | 8.9668 | 9.8215 | 10.7647 | 11.6576 | 12.7598 | 13.8323 | 14.7823 | 15.6548 | 16.5292 | 17.477 | 18.6323 | 19.7909 | 20.8426 | 21.9016 | 21.9016 | 25.121 | 26.2083 | 27.3028 | 28.4044 | 29.5131 | 30.6289 | 31.7519 | 32.8819 | 34.0191
| $500 - $1,000 | 2.2515 | 2.8902 | 3.5392 | 4.2376 | 4.8516 | 5.6158 | 6.3204 | 6.9228 | 7.5876 | 8.217 | 8.9939 | 9.7499 | 10.4195 | 11.0345 | 11.6508 | 12.3189 | 13.1332 | 13.9498 | 14.6912 | 15.4376 | 15.4376 | 17.7068 | 18.4733 | 19.2447 | 20.0212 | 20.8027 | 21.5892 | 22.3807 | 23.1772 | 23.9788
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 11.3882 | 14.6189 | 17.9017 | 21.4343 | 24.5402 | 28.4056 | 31.9693 | 35.0164 | 38.3791 | 41.5628 | 45.4923 | 49.3163 | 52.7033 | 55.8141 | 58.9315 | 62.3105 | 66.4296 | 70.5602 | 74.3101 | 78.0855 | 78.0855 | 89.5636 | 93.4403 | 97.3425 | 101.27 | 105.2229 | 109.2011 | 113.2047 | 117.2337 | 121.288
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 2.93 | 3.762 | 4.6431 | 5.5506 | 6.4077 | 7.312 | 8.2695 | 9.2163 | 10.1806 | 11.0565 | 11.9581 | 13.0218 | 14.0519 | 15.0213 | 16.0601 | 17.1054 | 18.0892 | 19.1628 | 20.2283 | 21.3057 | 21.3057 | 24.6101 | 25.7357 | 26.8732 | 28.0227 | 29.1843 | 30.3578 | 31.5434 | 32.741 | 33.9506
| $500 - $1,000 | 2.0653 | 2.6517 | 3.2728 | 3.9124 | 4.5165 | 5.1539 | 5.8289 | 6.4962 | 7.1759 | 7.7933 | 8.4288 | 9.1786 | 9.9047 | 10.5879 | 11.3202 | 12.0569 | 12.7504 | 13.5072 | 14.2582 | 15.0176 | 15.0176 | 17.3468 | 18.1401 | 18.9419 | 19.7522 | 20.5709 | 21.3981 | 22.2338 | 23.0779 | 23.9305
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 10.4464 | 13.4125 | 16.5541 | 19.7896 | 22.8452 | 26.0693 | 29.4832 | 32.8587 | 36.2967 | 39.4198 | 42.6342 | 46.4266 | 50.0991 | 53.5552 | 57.2589 | 60.9856 | 64.4932 | 68.3212 | 72.1197 | 75.9611 | 75.9611 | 87.7424 | 91.7551 | 95.8107 | 99.9092 | 104.0504 | 108.2346 | 112.4615 | 116.7313 | 121.0439
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tasmania
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 5.8484 | 6.0165 | 5.9282 | 6.0508 | 6.2067 | 6.3571 | 6.5266 | 6.6833 | 6.8983 | 7.0787 | 7.2692 | 7.3901 | 7.4919 | 7.6263 | 7.82 | 8.0395 | 8.1791 | 8.3766 | 8.5688 | 8.7628 | 8.7628 | 9.356 | 9.5574 | 9.7606 | 9.9657 | 10.1726 | 10.3814 | 10.592 | 10.8045 | 11.0188
| $500 - $1,000 | 13.9097 | 14.3095 | 14.0995 | 14.3912 | 14.7618 | 15.1196 | 15.5228 | 15.8953 | 16.4067 | 16.8358 | 17.2888 | 17.5765 | 17.8185 | 18.1383 | 18.599 | 19.121 | 19.4531 | 19.9228 | 20.3799 | 20.8413 | 20.8413 | 22.252 | 22.731 | 23.2144 | 23.7022 | 24.1943 | 24.6909 | 25.1918 | 25.6971 | 26.2068
| $1,000 - $7,500 | 0.52688 | 0.54203 | 0.53407 | 0.54512 | 0.55916 | 0.57271 | 0.58799 | 0.6021 | 0.62147 | 0.63772 | 0.65488 | 0.66578 | 0.67494 | 0.68706 | 0.70451 | 0.72428 | 0.73686 | 0.75465 | 0.77196 | 0.78944 | 0.78944 | 0.84288 | 0.86102 | 0.87933 | 0.89781 | 0.91645 | 0.93526 | 0.95423 | 0.97337 | 0.99268
| $7,500 - MPC | 2.4131 | 2.4825 | 2.446 | 2.4966 | 2.561 | 2.623 | 2.693 | 2.7576 | 2.8463 | 2.9208 | 2.9994 | 3.0493 | 3.0912 | 3.1467 | 3.2267 | 3.3172 | 3.3748 | 3.4563 | 3.5356 | 3.6157 | 3.6157 | 3.8604 | 3.9435 | 4.0273 | 4.112 | 4.1973 | 4.2835 | 4.3704 | 4.4581 | 4.5465
| MPC | 1.7566 | 1.8071 | 1.7805 | 1.8174 | 1.8642 | 1.9094 | 1.9603 | 2.0073 | 2.0719 | 2.1261 | 2.1833 | 2.2196 | 2.2502 | 2.2906 | 2.3488 | 2.4147 | 2.4566 | 2.5159 | 2.5737 | 2.6319 | 2.6319 | 2.8101 | 2.8706 | 2.9316 | 2.9932 | 3.0554 | 3.1181 | 3.1813 | 3.2451 | 3.3095
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 6.0326 | 6.2787 | 6.3105 | 6.5137 | 6.7633 | 6.9532 | 7.2233 | 7.5291 | 7.7943 | 8.086 | 8.3041 | 8.5499 | 8.7832 | 8.9899 | 9.2229 | 9.5133 | 9.7964 | 10.0695 | 10.3458 | 10.6246 | 10.6246 | 11.4761 | 11.765 | 12.0565 | 12.3505 | 12.647 | 12.9461 | 13.2477 | 13.5518 | 13.8585
| $500 - $1,000 | 14.3478 | 14.933 | 15.0088 | 15.492 | 16.0856 | 16.5373 | 17.1798 | 17.907 | 18.5378 | 19.2315 | 19.7504 | 20.3348 | 20.8897 | 21.3814 | 21.9355 | 22.6263 | 23.2995 | 23.9492 | 24.6062 | 25.2692 | 25.2692 | 27.2945 | 27.9817 | 28.6749 | 29.3741 | 30.0794 | 30.7906 | 31.5079 | 32.2313 | 32.9607
| $1,000 - $7,500 | 0.54348 | 0.56565 | 0.56851 | 0.58682 | 0.6093 | 0.62641 | 0.65075 | 0.67829 | 0.70219 | 0.72847 | 0.74812 | 0.77026 | 0.79128 | 0.8099 | 0.83089 | 0.85705 | 0.88256 | 0.90717 | 0.93205 | 0.95717 | 0.95717 | 1.0339 | 1.0599 | 1.0862 | 1.1127 | 1.1394 | 1.1663 | 1.1935 | 1.2209 | 1.2485
| $7,500 - MPC | 2.4891 | 2.5907 | 2.6038 | 2.6876 | 2.7906 | 2.869 | 2.9804 | 3.1066 | 3.216 | 3.3364 | 3.4264 | 3.5278 | 3.6241 | 3.7094 | 3.8055 | 3.9253 | 4.0421 | 4.1548 | 4.2688 | 4.3838 | 4.3838 | 4.7352 | 4.8544 | 4.9747 | 5.096 | 5.2183 | 5.3417 | 5.4662 | 5.5916 | 5.7182
| MPC | 1.8119 | 1.8858 | 1.8954 | 1.9564 | 2.0314 | 2.0884 | 2.1695 | 2.2614 | 2.341 | 2.4286 | 2.4942 | 2.568 | 2.638 | 2.7001 | 2.7701 | 2.8573 | 2.9424 | 3.0244 | 3.1074 | 3.1911 | 3.1911 | 3.4469 | 3.5337 | 3.6212 | 3.7095 | 3.7986 | 3.8884 | 3.979 | 4.0703 | 4.1624
Strong
Queensland
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 37.1698 | 40.7993 | 43.4656 | 46.9013 | 49.7357 | 52.0509 | 55.5269 | 60.1367 | 63.3705 | 65.9977 | 69.376 | 71.4842 | 74.2128 | 79.2005 | 82.8291 | 86.2015 | 90.0765 | 90.8142 | 94.3351 | 97.8911 | 97.8911 | 108.7695 | 112.4658 | 116.1972 | 119.9637 | 123.7653 | 127.6019 | 131.4737 | 135.3805 | 139.3224
| $500 - $1,000 | 0.41223 | 0.45249 | 0.48206 | 0.52016 | 0.5516 | 0.57727 | 0.61582 | 0.66695 | 0.70281 | 0.73195 | 0.76942 | 0.7928 | 0.82306 | 0.87838 | 0.91862 | 0.95602 | 0.999 | 1.0072 | 1.0462 | 1.0857 | 1.0857 | 1.2063 | 1.2473 | 1.2887 | 1.3305 | 1.3726 | 1.4152 | 1.4581 | 1.5014 | 1.5452
| $1,000 - $7,500 | 1.2482 | 1.37 | 1.4596 | 1.5749 | 1.6701 | 1.7479 | 1.8646 | 2.0194 | 2.128 | 2.2162 | 2.3296 | 2.4004 | 2.4921 | 2.6595 | 2.7814 | 2.8946 | 3.0248 | 3.0495 | 3.1678 | 3.2872 | 3.2872 | 3.6525 | 3.7766 | 3.9019 | 4.0284 | 4.156 | 4.2848 | 4.4149 | 4.546 | 4.6784
| $7,500 - MPC | 7.3172 | 8.0316 | 8.5565 | 9.2329 | 9.7909 | 10.2466 | 10.9309 | 11.8384 | 12.475 | 12.9921 | 13.6572 | 14.0722 | 14.6094 | 15.5912 | 16.3056 | 16.9694 | 17.7323 | 17.8775 | 18.5706 | 19.2706 | 19.2706 | 21.4121 | 22.1398 | 22.8743 | 23.6158 | 24.3641 | 25.1194 | 25.8816 | 26.6507 | 27.4267
| MPC | 201.617 | 221.3039 | 235.7667 | 254.4029 | 269.7773 | 282.3354 | 301.1896 | 326.1944 | 343.7351 | 357.9855 | 376.3101 | 387.7459 | 402.5462 | 429.6007 | 449.283 | 467.5756 | 488.5944 | 492.5957 | 511.6937 | 530.9821 | 530.9821 | 589.9891 | 610.0387 | 630.2786 | 650.7088 | 671.3293 | 692.1402 | 713.1413 | 734.3327 | 755.7144
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 38.0183 | 41.1759 | 44.1916 | 47.0181 | 49.6679 | 52.621 | 56.9188 | 60.0547 | 62.9765 | 65.5708 | 68.4285 | 71.8373 | 75.2761 | 78.2355 | 81.1959 | 83.8149 | 87.3673 | 90.8072 | 94.3267 | 97.8842 | 97.8842 | 108.7854 | 112.4954 | 116.2434 | 120.0295 | 123.8537 | 127.716 | 131.6165 | 135.555 | 139.5315
| $500 - $1,000 | 0.42164 | 0.45666 | 0.49011 | 0.52146 | 0.55085 | 0.5836 | 0.63126 | 0.66604 | 0.69844 | 0.72722 | 0.75891 | 0.79672 | 0.83486 | 0.86768 | 0.90051 | 0.92956 | 0.96895 | 1.0071 | 1.0461 | 1.0856 | 1.0856 | 1.2065 | 1.2476 | 1.2892 | 1.3312 | 1.3736 | 1.4164 | 1.4597 | 1.5034 | 1.5475
| $1,000 - $7,500 | 1.2766 | 1.3827 | 1.4839 | 1.5789 | 1.6678 | 1.767 | 1.9113 | 2.0166 | 2.1147 | 2.2019 | 2.2978 | 2.4123 | 2.5278 | 2.6271 | 2.7265 | 2.8145 | 2.9338 | 3.0493 | 3.1675 | 3.2869 | 3.2869 | 3.653 | 3.7776 | 3.9034 | 4.0306 | 4.159 | 4.2887 | 4.4197 | 4.5519 | 4.6854
| $7,500 - MPC | 7.4842 | 8.1058 | 8.6995 | 9.2559 | 9.7775 | 10.3589 | 11.2049 | 11.8222 | 12.3974 | 12.9081 | 13.4707 | 14.1417 | 14.8187 | 15.4013 | 15.984 | 16.4996 | 17.1989 | 17.8761 | 18.5689 | 19.2693 | 19.2693 | 21.4152 | 22.1456 | 22.8834 | 23.6287 | 24.3816 | 25.1419 | 25.9097 | 26.685 | 27.4679
| MPC | 182.7945 | 197.9768 | 212.4763 | 226.0664 | 238.807 | 253.0057 | 273.6697 | 288.7471 | 302.7953 | 315.269 | 329.0093 | 345.3991 | 361.9329 | 376.1618 | 390.3955 | 402.9881 | 420.0684 | 436.6076 | 453.5294 | 470.6343 | 470.6343 | 523.0482 | 540.8858 | 558.9066 | 577.1105 | 595.4976 | 614.0679 | 632.8213 | 651.7579 | 670.8777
New South Wales
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 126.8519 | 151.8192 | 176.5757 | 199.9942 | 225.9737 | 253.9989 | 278.5219 | 309.1274 | 333.1624 | 358.1545 | 387.5127 | 412.5448 | 439.2906 | 469.7517 | 492.0782 | 523.2652 | 559.3418 | 590.8385 | 622.0772 | 653.7028 | 653.7028 | 750.9005 | 784.0734 | 817.6332 | 851.5797 | 885.9131 | 920.6333 | 955.7403 | 991.2342 | 1027.1149
| $500 - $1,000 | 0.44063 | 0.52735 | 0.61335 | 0.69469 | 0.78493 | 0.88228 | 0.96746 | 1.0738 | 1.1573 | 1.2441 | 1.346 | 1.433 | 1.5259 | 1.6317 | 1.7093 | 1.8176 | 1.9429 | 2.0523 | 2.1608 | 2.2707 | 2.2707 | 2.6083 | 2.7235 | 2.8401 | 2.958 | 3.0773 | 3.1979 | 3.3198 | 3.4431 | 3.5677
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 44.0791 | 52.7549 | 61.3574 | 69.495 | 78.5225 | 88.2608 | 96.7821 | 107.4171 | 115.7689 | 124.4533 | 134.6548 | 143.3531 | 152.6468 | 163.2316 | 170.9897 | 181.8267 | 194.3628 | 205.3074 | 216.1624 | 227.1519 | 227.1519 | 260.9266 | 272.4537 | 284.1152 | 295.9111 | 307.8414 | 319.9062 | 332.1053 | 344.4389 | 356.9069
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 123.2241 | 146.852 | 170.0697 | 194.4421 | 215.5349 | 240.6048 | 266.5367 | 290.9246 | 316.3731 | 336.7103 | 361.6822 | 384.5123 | 410.448 | 435.4217 | 461.4406 | 483.1775 | 511.1711 | 535.8229 | 561.2308 | 586.7618 | 586.7618 | 664.0929 | 690.116 | 716.2621 | 742.5313 | 768.9236 | 795.4389 | 822.0772 | 848.8385 | 875.7229
| $500 - $1,000 | 0.42803 | 0.5101 | 0.59075 | 0.67541 | 0.74867 | 0.83576 | 0.92583 | 1.0105 | 1.0989 | 1.1696 | 1.2563 | 1.3356 | 1.4257 | 1.5125 | 1.6028 | 1.6783 | 1.7756 | 1.8612 | 1.9495 | 2.0382 | 2.0382 | 2.3068 | 2.3972 | 2.488 | 2.5792 | 2.6709 | 2.763 | 2.8555 | 2.9485 | 3.0419
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 42.8185 | 51.0289 | 59.0967 | 67.5657 | 74.8951 | 83.6065 | 92.6175 | 101.0919 | 109.9349 | 117.0017 | 125.6791 | 133.6122 | 142.6245 | 151.3024 | 160.3436 | 167.8969 | 177.6242 | 186.1904 | 195.0192 | 203.8908 | 203.8908 | 230.7622 | 239.8049 | 248.8903 | 258.0184 | 267.1893 | 276.403 | 285.6594 | 294.9586 | 304.3005
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victoria
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 44.655 | 52.9262 | 61.1607 | 68.83 | 79.1677 | 88.382 | 97.5547 | 107.5022 | 115.6123 | 123.798 | 133.9254 | 142.2641 | 151.6663 | 159.6314 | 166.2229 | 182.4354 | 192.7905 | 202.7611 | 214.0022 | 225.4268 | 225.4268 | 260.8014 | 272.9599 | 285.3019 | 297.8273 | 310.5362 | 323.4285 | 336.5044 | 349.7637 | 363.2065
| $500 - $1,000 | 4.7838 | 5.6698 | 6.552 | 7.3736 | 8.481 | 9.4681 | 10.4508 | 11.5164 | 12.3852 | 13.2621 | 14.3471 | 15.2404 | 16.2476 | 17.1009 | 17.807 | 19.5438 | 20.6531 | 21.7212 | 22.9255 | 24.1493 | 24.1493 | 27.9389 | 29.2414 | 30.5636 | 31.9054 | 33.2669 | 34.648 | 36.0488 | 37.4692 | 38.9093
| $1,000 - $7,500 | 2.5178 | 2.9841 | 3.4484 | 3.8808 | 4.4637 | 4.9832 | 5.5004 | 6.0613 | 6.5185 | 6.9801 | 7.5511 | 8.0212 | 8.5514 | 9.0005 | 9.3721 | 10.2862 | 10.8701 | 11.4322 | 12.066 | 12.7102 | 12.7102 | 14.7047 | 15.3902 | 16.0861 | 16.7923 | 17.5089 | 18.2358 | 18.973 | 19.7206 | 20.4786
| $7,500 - MPC | 1.0386 | 1.231 | 1.4225 | 1.6008 | 1.8413 | 2.0556 | 2.2689 | 2.5003 | 2.6889 | 2.8793 | 3.1148 | 3.3088 | 3.5274 | 3.7127 | 3.866 | 4.2431 | 4.4839 | 4.7158 | 4.9772 | 5.243 | 5.243 | 6.0657 | 6.3485 | 6.6355 | 6.9268 | 7.2224 | 7.5223 | 7.8264 | 8.1348 | 8.4474
| MPC | 68.4519 | 81.1309 | 93.7536 | 105.5099 | 121.3566 | 135.4813 | 149.5422 | 164.7907 | 177.2227 | 189.7706 | 205.2951 | 218.0775 | 232.4901 | 244.6999 | 254.804 | 279.6564 | 295.5296 | 310.8137 | 328.0453 | 345.5581 | 345.5581 | 399.784 | 418.4218 | 437.3409 | 456.5412 | 476.0227 | 495.7855 | 515.8295 | 536.1548 | 556.7613
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 55.8353 | 69.5673 | 84.0319 | 98.4561 | 113.2009 | 128.7267 | 143.2602 | 158.0867 | 174.0511 | 187.0908 | 201.6314 | 217.202 | 232.053 | 247.5899 | 262.2023 | 277.5009 | 294.4607 | 311.0968 | 327.2947 | 343.6211 | 343.6211 | 393.371 | 410.2113 | 427.18 | 444.2773 | 461.5029 | 478.8571 | 496.3397 | 513.9508 | 531.6904
| $500 - $1,000 | 5.9815 | 7.4526 | 9.0021 | 10.5473 | 12.1269 | 13.7901 | 15.3471 | 16.9354 | 18.6456 | 20.0425 | 21.6002 | 23.2682 | 24.8592 | 26.5236 | 28.089 | 29.7279 | 31.5448 | 33.3269 | 35.0622 | 36.8112 | 36.8112 | 42.1407 | 43.9448 | 45.7626 | 47.5942 | 49.4395 | 51.2986 | 53.1715 | 55.0581 | 56.9585
| $1,000 - $7,500 | 3.1481 | 3.9224 | 4.738 | 5.5512 | 6.3826 | 7.258 | 8.0774 | 8.9134 | 9.8135 | 10.5487 | 11.3685 | 12.2464 | 13.0838 | 13.9598 | 14.7837 | 15.6463 | 16.6025 | 17.5405 | 18.4538 | 19.3743 | 19.3743 | 22.1793 | 23.1288 | 24.0856 | 25.0496 | 26.0208 | 26.9993 | 27.985 | 28.978 | 29.9782
| $7,500 - MPC | 1.2986 | 1.618 | 1.9544 | 2.2899 | 2.6328 | 2.9939 | 3.3319 | 3.6768 | 4.0481 | 4.3513 | 4.6895 | 5.0517 | 5.3971 | 5.7584 | 6.0983 | 6.4541 | 6.8485 | 7.2355 | 7.6122 | 7.9919 | 7.9919 | 9.149 | 9.5406 | 9.9353 | 10.3329 | 10.7336 | 11.1372 | 11.5438 | 11.9534 | 12.366
| MPC | 12.7893 | 15.9347 | 19.2479 | 22.5519 | 25.9292 | 29.4855 | 32.8144 | 36.2105 | 39.8673 | 42.8541 | 46.1847 | 49.7512 | 53.1529 | 56.7117 | 60.0587 | 63.5629 | 67.4477 | 71.2582 | 74.9685 | 78.7081 | 78.7081 | 90.1036 | 93.9609 | 97.8477 | 101.7639 | 105.7095 | 109.6846 | 113.689 | 117.723 | 121.7863
South Australia
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 4.206 | 5.5475 | 6.9365 | 8.3085 | 9.7354 | 11.351 | 12.8297 | 14.144 | 15.5487 | 16.7871 | 18.3041 | 19.7434 | 21.2268 | 22.4805 | 23.7152 | 25.3123 | 27.1335 | 28.6408 | 30.2105 | 31.7922 | 31.7922 | 36.6086 | 38.2378 | 39.8789 | 41.5319 | 43.1968 | 44.8736 | 46.5623 | 48.2628 | 49.9753
| $500 - $1,000 | 2.9647 | 3.9103 | 4.8893 | 5.8564 | 6.8622 | 8.0009 | 9.0432 | 9.9696 | 10.9597 | 11.8326 | 12.9019 | 13.9164 | 14.962 | 15.8457 | 16.7159 | 17.8417 | 19.1254 | 20.1878 | 21.2943 | 22.4091 | 22.4091 | 25.804 | 26.9524 | 28.1092 | 29.2743 | 30.4478 | 31.6297 | 32.82 | 34.0186 | 35.2257
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 14.9956 | 19.7786 | 24.7306 | 29.6223 | 34.7097 | 40.4697 | 45.7415 | 50.4276 | 55.4358 | 59.851 | 65.2595 | 70.391 | 75.6799 | 80.1495 | 84.5515 | 90.2459 | 96.739 | 102.1127 | 107.7094 | 113.3486 | 113.3486 | 130.5203 | 136.329 | 142.18 | 148.0735 | 154.0093 | 159.9875 | 166.0081 | 172.0711 | 178.1764
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 3.883 | 5.1948 | 6.4998 | 7.8362 | 9.101 | 10.4031 | 11.7923 | 13.163 | 14.4541 | 15.6651 | 16.8378 | 18.1251 | 19.5999 | 20.8973 | 22.2441 | 23.6157 | 24.7861 | 26.1414 | 27.4524 | 28.7632 | 28.7632 | 32.6957 | 34.0064 | 35.3171 | 36.6278 | 37.9384 | 39.249 | 40.5595 | 41.87 | 43.1805
| $500 - $1,000 | 2.737 | 3.6616 | 4.5815 | 5.5235 | 6.4149 | 7.3327 | 8.3119 | 9.2781 | 10.1882 | 11.0417 | 11.8683 | 12.7757 | 13.8152 | 14.7297 | 15.6791 | 16.6458 | 17.4708 | 18.4261 | 19.3501 | 20.2741 | 20.2741 | 23.046 | 23.9699 | 24.8937 | 25.8175 | 26.7413 | 27.6651 | 28.5889 | 29.5126 | 30.4363
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 13.844 | 18.521 | 23.1737 | 27.9385 | 32.4477 | 37.0901 | 42.0429 | 46.9298 | 51.5332 | 55.8507 | 60.0317 | 64.6213 | 69.8795 | 74.505 | 79.3069 | 84.197 | 88.3698 | 93.2019 | 97.8757 | 102.5494 | 102.5494 | 116.5697 | 121.2429 | 125.9159 | 130.5887 | 135.2615 | 139.9341 | 144.6065 | 149.2788 | 153.951
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tasmania
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 6.1368 | 6.4151 | 6.4474 | 6.7338 | 6.9858 | 7.2793 | 7.6076 | 7.9156 | 8.2754 | 8.6004 | 8.8678 | 9.1692 | 9.4339 | 9.6614 | 10.0128 | 10.3676 | 10.7166 | 10.9872 | 11.3252 | 11.6656 | 11.6656 | 12.7026 | 13.0534 | 13.4067 | 13.7627 | 14.1212 | 14.4823 | 14.846 | 15.2122 | 15.5811
| $500 - $1,000 | 14.5957 | 15.2575 | 15.3343 | 16.0155 | 16.6148 | 17.313 | 18.0936 | 18.8264 | 19.682 | 20.455 | 21.091 | 21.8078 | 22.4374 | 22.9784 | 23.8143 | 24.6581 | 25.488 | 26.1318 | 26.9355 | 27.7453 | 27.7453 | 30.2115 | 31.0458 | 31.8863 | 32.7328 | 33.5856 | 34.4444 | 35.3094 | 36.1805 | 37.0577
| $1,000 - $7,500 | 0.55287 | 0.57793 | 0.58084 | 0.60665 | 0.62935 | 0.65579 | 0.68537 | 0.71312 | 0.74553 | 0.77481 | 0.7989 | 0.82605 | 0.8499 | 0.8704 | 0.90206 | 0.93402 | 0.96546 | 0.98984 | 1.0203 | 1.051 | 1.051 | 1.1444 | 1.176 | 1.2078 | 1.2399 | 1.2722 | 1.3047 | 1.3375 | 1.3705 | 1.4037
| $7,500 - MPC | 2.5321 | 2.6469 | 2.6603 | 2.7784 | 2.8824 | 3.0035 | 3.139 | 3.2661 | 3.4145 | 3.5486 | 3.659 | 3.7833 | 3.8925 | 3.9864 | 4.1314 | 4.2778 | 4.4218 | 4.5335 | 4.6729 | 4.8134 | 4.8134 | 5.2412 | 5.386 | 5.5318 | 5.6787 | 5.8266 | 5.9756 | 6.1256 | 6.2768 | 6.4289
| MPC | 1.8432 | 1.9268 | 1.9365 | 2.0225 | 2.0982 | 2.1864 | 2.2849 | 2.3775 | 2.4855 | 2.5832 | 2.6635 | 2.754 | 2.8335 | 2.9018 | 3.0074 | 3.1139 | 3.2187 | 3.3 | 3.4015 | 3.5038 | 3.5038 | 3.8152 | 3.9206 | 4.0267 | 4.1336 | 4.2413 | 4.3498 | 4.459 | 4.569 | 4.6798
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 6.3293 | 6.709 | 6.8833 | 7.2426 | 7.6369 | 8.0365 | 8.4674 | 8.9292 | 9.342 | 9.7796 | 10.197 | 10.5463 | 10.9239 | 11.289 | 11.7284 | 12.1782 | 12.6026 | 13.0134 | 13.4504 | 13.8897 | 13.8897 | 15.2221 | 15.671 | 16.1222 | 16.5758 | 17.0318 | 17.4901 | 17.9509 | 18.4139 | 18.8794
| $500 - $1,000 | 15.0534 | 15.9566 | 16.371 | 17.2256 | 18.1634 | 19.1138 | 20.1387 | 21.2369 | 22.2189 | 23.2595 | 24.2522 | 25.0831 | 25.9812 | 26.8495 | 27.8945 | 28.9643 | 29.9737 | 30.9507 | 31.9901 | 33.0351 | 33.0351 | 36.204 | 37.2715 | 38.3447 | 39.4236 | 40.5081 | 41.5982 | 42.6939 | 43.7953 | 44.9024
| $1,000 - $7,500 | 0.5702 | 0.60442 | 0.62011 | 0.65249 | 0.68801 | 0.72401 | 0.76283 | 0.80443 | 0.84162 | 0.88104 | 0.91864 | 0.95012 | 0.98414 | 1.017 | 1.0566 | 1.0971 | 1.1354 | 1.1724 | 1.2117 | 1.2513 | 1.2513 | 1.3714 | 1.4118 | 1.4525 | 1.4933 | 1.5344 | 1.5757 | 1.6172 | 1.6589 | 1.7008
| $7,500 - MPC | 2.6115 | 2.7682 | 2.8401 | 2.9884 | 3.1511 | 3.316 | 3.4938 | 3.6843 | 3.8546 | 4.0352 | 4.2074 | 4.3515 | 4.5073 | 4.658 | 4.8393 | 5.0249 | 5.2 | 5.3695 | 5.5498 | 5.7311 | 5.7311 | 6.2808 | 6.466 | 6.6522 | 6.8394 | 7.0275 | 7.2167 | 7.4068 | 7.5978 | 7.7899
| MPC | 1.901 | 2.0151 | 2.0674 | 2.1753 | 2.2937 | 2.4138 | 2.5432 | 2.6819 | 2.8059 | 2.9373 | 3.0627 | 3.1676 | 3.281 | 3.3907 | 3.5226 | 3.6577 | 3.7852 | 3.9086 | 4.0398 | 4.1718 | 4.1718 | 4.572 | 4.7068 | 4.8423 | 4.9786 | 5.1155 | 5.2532 | 5.3916 | 5.5307 | 5.6705
Weak
Queensland
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 32.2053 | 33.0832 | 33.0322 | 33.1417 | 33.5322 | 33.0302 | 33.5945 | 34.6407 | 35.0112 | 34.8193 | 34.7606 | 34.3475 | 34.2557 | 34.9482 | 35.1158 | 35.3714 | 35.451 | 34.4576 | 34.664 | 34.8703 | 34.8703 | 35.4892 | 35.6956 | 35.9019 | 36.1082 | 36.3145 | 36.5208 | 36.7272 | 36.9335 | 37.1398
| $500 - $1,000 | 0.35718 | 0.36691 | 0.36635 | 0.36756 | 0.37189 | 0.36632 | 0.37258 | 0.38419 | 0.38829 | 0.38617 | 0.38552 | 0.38093 | 0.37992 | 0.3876 | 0.38945 | 0.39229 | 0.39317 | 0.38215 | 0.38444 | 0.38673 | 0.38673 | 0.3936 | 0.39588 | 0.39817 | 0.40046 | 0.40275 | 0.40504 | 0.40733 | 0.40961 | 0.4119
| $1,000 - $7,500 | 1.0814 | 1.1109 | 1.1092 | 1.1129 | 1.126 | 1.1091 | 1.1281 | 1.1632 | 1.1757 | 1.1692 | 1.1673 | 1.1534 | 1.1503 | 1.1736 | 1.1792 | 1.1878 | 1.1904 | 1.1571 | 1.164 | 1.1709 | 1.1709 | 1.1917 | 1.1986 | 1.2056 | 1.2125 | 1.2194 | 1.2264 | 1.2333 | 1.2402 | 1.2471
| $7,500 - MPC | 6.3399 | 6.5127 | 6.5026 | 6.5242 | 6.6011 | 6.5022 | 6.6133 | 6.8193 | 6.8922 | 6.8544 | 6.8429 | 6.7616 | 6.7435 | 6.8798 | 6.9128 | 6.9631 | 6.9788 | 6.7832 | 6.8239 | 6.8645 | 6.8645 | 6.9863 | 7.0269 | 7.0676 | 7.1082 | 7.1488 | 7.1894 | 7.23 | 7.2706 | 7.3113
| MPC | 174.6884 | 179.4501 | 179.1739 | 179.7678 | 181.8861 | 179.1627 | 182.2237 | 187.8988 | 189.9082 | 188.8674 | 188.549 | 186.308 | 185.8103 | 189.5667 | 190.4758 | 191.862 | 192.2936 | 186.9056 | 188.0247 | 189.1438 | 189.1438 | 192.5012 | 193.6204 | 194.7395 | 195.8586 | 196.9777 | 198.0969 | 199.216 | 200.3351 | 201.4543
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 32.9898 | 33.4978 | 33.93 | 34.1711 | 34.2412 | 34.54 | 35.6044 | 36.0336 | 36.2186 | 36.1085 | 36.4755 | 36.8712 | 37.2451 | 37.437 | 37.4246 | 37.3218 | 38.062 | 37.8934 | 38.1309 | 38.3684 | 38.3684 | 39.0808 | 39.3183 | 39.5557 | 39.7932 | 40.0307 | 40.2682 | 40.5056 | 40.7431 | 40.9806
| $500 - $1,000 | 0.36588 | 0.37151 | 0.3763 | 0.37898 | 0.37975 | 0.38307 | 0.39487 | 0.39963 | 0.40168 | 0.40046 | 0.40453 | 0.40892 | 0.41307 | 0.4152 | 0.41506 | 0.41392 | 0.42213 | 0.42026 | 0.42289 | 0.42553 | 0.42553 | 0.43343 | 0.43606 | 0.4387 | 0.44133 | 0.44396 | 0.4466 | 0.44923 | 0.45186 | 0.4545
| $1,000 - $7,500 | 1.1078 | 1.1248 | 1.1394 | 1.1475 | 1.1498 | 1.1598 | 1.1956 | 1.21 | 1.2162 | 1.2125 | 1.2248 | 1.2381 | 1.2507 | 1.2571 | 1.2567 | 1.2533 | 1.2781 | 1.2725 | 1.2804 | 1.2884 | 1.2884 | 1.3123 | 1.3203 | 1.3283 | 1.3362 | 1.3442 | 1.3522 | 1.3602 | 1.3681 | 1.3761
| $7,500 - MPC | 6.4943 | 6.5943 | 6.6794 | 6.7268 | 6.7406 | 6.7995 | 7.009 | 7.0935 | 7.1299 | 7.1082 | 7.1805 | 7.2584 | 7.332 | 7.3698 | 7.3673 | 7.3471 | 7.4928 | 7.4596 | 7.5064 | 7.5531 | 7.5531 | 7.6934 | 7.7401 | 7.7869 | 7.8336 | 7.8803 | 7.9271 | 7.9738 | 8.0206 | 8.0673
| MPC | 158.6175 | 161.0598 | 163.1376 | 164.2971 | 164.6341 | 166.0709 | 171.1885 | 173.2523 | 174.1414 | 173.6124 | 175.3766 | 177.2794 | 179.0773 | 179.9997 | 179.9403 | 179.4459 | 183.0047 | 182.1944 | 183.3362 | 184.478 | 184.478 | 187.9033 | 189.0451 | 190.1869 | 191.3287 | 192.4704 | 193.6122 | 194.754 | 195.8958 | 197.0376
New South Wales
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 77.6913 | 78.3968 | 78.4007 | 78.568 | 78.5777 | 79.8719 | 81.2272 | 82.4161 | 82.0305 | 81.8411 | 83.147 | 82.7215 | 82.8984 | 83.5999 | 83.7869 | 84.1972 | 86.2372 | 85.7714 | 86.3142 | 86.8571 | 86.8571 | 88.4857 | 89.0286 | 89.5714 | 90.1143 | 90.6571 | 91.2 | 91.7429 | 92.2857 | 92.8286
| $500 - $1,000 | 0.26987 | 0.27232 | 0.27233 | 0.27291 | 0.27294 | 0.27744 | 0.28215 | 0.28628 | 0.28494 | 0.28428 | 0.28882 | 0.28734 | 0.28795 | 0.29039 | 0.29104 | 0.29246 | 0.29955 | 0.29793 | 0.29982 | 0.3017 | 0.3017 | 0.30736 | 0.30925 | 0.31113 | 0.31302 | 0.3149 | 0.31679 | 0.31867 | 0.32056 | 0.32245
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 26.9966 | 27.2417 | 27.2431 | 27.3012 | 27.3046 | 27.7543 | 28.2252 | 28.6384 | 28.5043 | 28.4386 | 28.8923 | 28.7445 | 28.8059 | 29.0497 | 29.1147 | 29.2572 | 29.9661 | 29.8043 | 29.9929 | 30.1815 | 30.1815 | 30.7474 | 30.9361 | 31.1247 | 31.3134 | 31.502 | 31.6906 | 31.8793 | 32.0679 | 32.2565
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 78.405 | 79.0881 | 79.7768 | 80.7923 | 80.8109 | 82.4225 | 84.0113 | 85.1329 | 86.2064 | 86.0342 | 86.6982 | 88.1715 | 88.8118 | 90.1206 | 91.7168 | 91.647 | 93.8397 | 93.9344 | 94.8879 | 95.8413 | 95.8413 | 98.7017 | 99.6552 | 100.6086 | 101.5621 | 102.5155 | 103.469 | 104.4225 | 105.3759 | 106.3294
| $500 - $1,000 | 0.27234 | 0.27472 | 0.27711 | 0.28064 | 0.2807 | 0.2863 | 0.29182 | 0.29571 | 0.29944 | 0.29885 | 0.30115 | 0.30627 | 0.30849 | 0.31304 | 0.31858 | 0.31834 | 0.32596 | 0.32629 | 0.3296 | 0.33291 | 0.33291 | 0.34285 | 0.34616 | 0.34947 | 0.35278 | 0.35609 | 0.35941 | 0.36272 | 0.36603 | 0.36934
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 27.2445 | 27.4819 | 27.7212 | 28.0741 | 28.0806 | 28.6406 | 29.1927 | 29.5824 | 29.9554 | 29.8956 | 30.1263 | 30.6383 | 30.8608 | 31.3155 | 31.8702 | 31.8459 | 32.6079 | 32.6408 | 32.9721 | 33.3034 | 33.3034 | 34.2973 | 34.6287 | 34.96 | 35.2913 | 35.6226 | 35.9539 | 36.2852 | 36.6165 | 36.9479
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victoria
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 27.9064 | 28.3152 | 27.609 | 26.8461 | 27.2408 | 27.2198 | 27.3301 | 27.5852 | 27.6233 | 27.8881 | 27.7667 | 28.0869 | 28.3199 | 28.128 | 27.8409 | 28.4521 | 28.9027 | 28.6505 | 28.7811 | 28.9117 | 28.9117 | 29.3035 | 29.4341 | 29.5647 | 29.6953 | 29.8259 | 29.9565 | 30.0871 | 30.2177 | 30.3483
| $500 - $1,000 | 2.9895 | 3.0333 | 2.9577 | 2.8759 | 2.9182 | 2.916 | 2.9278 | 2.9551 | 2.9592 | 2.9876 | 2.9746 | 3.0089 | 3.0338 | 3.0133 | 2.9825 | 3.048 | 3.0963 | 3.0692 | 3.0832 | 3.0972 | 3.0972 | 3.1392 | 3.1532 | 3.1672 | 3.1812 | 3.1952 | 3.2092 | 3.2231 | 3.2371 | 3.2511
| $1,000 - $7,500 | 1.5734 | 1.5965 | 1.5567 | 1.5137 | 1.5359 | 1.5347 | 1.5409 | 1.5553 | 1.5575 | 1.5724 | 1.5656 | 1.5836 | 1.5968 | 1.5859 | 1.5697 | 1.6042 | 1.6296 | 1.6154 | 1.6228 | 1.6301 | 1.6301 | 1.6522 | 1.6596 | 1.6669 | 1.6743 | 1.6817 | 1.689 | 1.6964 | 1.7038 | 1.7111
| $7,500 - MPC | 0.64904 | 0.65855 | 0.64213 | 0.62438 | 0.63356 | 0.63307 | 0.63564 | 0.64157 | 0.64246 | 0.64862 | 0.64579 | 0.65324 | 0.65866 | 0.6542 | 0.64752 | 0.66174 | 0.67222 | 0.66635 | 0.66939 | 0.67242 | 0.67242 | 0.68154 | 0.68457 | 0.68761 | 0.69065 | 0.69369 | 0.69672 | 0.69976 | 0.7028 | 0.70584
| MPC | 42.7779 | 43.4045 | 42.322 | 41.1525 | 41.7576 | 41.7254 | 41.8945 | 42.2855 | 42.344 | 42.7498 | 42.5637 | 43.0546 | 43.4117 | 43.1176 | 42.6775 | 43.6144 | 44.3051 | 43.9185 | 44.1187 | 44.3189 | 44.3189 | 44.9195 | 45.1197 | 45.3199 | 45.5201 | 45.7203 | 45.9205 | 46.1207 | 46.3209 | 46.5211
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 28.7314 | 28.8428 | 28.5782 | 28.5394 | 28.4173 | 28.2126 | 28.8496 | 29.0621 | 29.4677 | 29.575 | 29.5023 | 30.1406 | 30.4026 | 30.4779 | 30.788 | 31.0508 | 31.4567 | 31.8964 | 32.251 | 32.6057 | 32.6057 | 33.6695 | 34.0242 | 34.3788 | 34.7334 | 35.088 | 35.4427 | 35.7973 | 36.1519 | 36.5065
| $500 - $1,000 | 3.0779 | 3.0898 | 3.0615 | 3.0573 | 3.0443 | 3.0223 | 3.0906 | 3.1133 | 3.1568 | 3.1683 | 3.1605 | 3.2289 | 3.257 | 3.265 | 3.2982 | 3.3264 | 3.3699 | 3.417 | 3.455 | 3.493 | 3.493 | 3.6069 | 3.6449 | 3.6829 | 3.7209 | 3.7589 | 3.7969 | 3.8349 | 3.8729 | 3.9108
| $1,000 - $7,500 | 1.62 | 1.6262 | 1.6113 | 1.6091 | 1.6022 | 1.5907 | 1.6266 | 1.6386 | 1.6615 | 1.6675 | 1.6634 | 1.6994 | 1.7142 | 1.7184 | 1.7359 | 1.7507 | 1.7736 | 1.7984 | 1.8184 | 1.8384 | 1.8384 | 1.8984 | 1.9184 | 1.9384 | 1.9584 | 1.9784 | 1.9984 | 2.0183 | 2.0383 | 2.0583
| $7,500 - MPC | 0.66823 | 0.67082 | 0.66467 | 0.66377 | 0.66093 | 0.65617 | 0.67098 | 0.67592 | 0.68536 | 0.68785 | 0.68616 | 0.70101 | 0.7071 | 0.70885 | 0.71606 | 0.72217 | 0.73162 | 0.74184 | 0.75009 | 0.75834 | 0.75834 | 0.78308 | 0.79133 | 0.79958 | 0.80783 | 0.81607 | 0.82432 | 0.83257 | 0.84082 | 0.84906
| MPC | 6.5811 | 6.6066 | 6.546 | 6.5371 | 6.5091 | 6.4622 | 6.6081 | 6.6568 | 6.7497 | 6.7743 | 6.7576 | 6.9039 | 6.9639 | 6.9811 | 7.0521 | 7.1123 | 7.2053 | 7.306 | 7.3873 | 7.4685 | 7.4685 | 7.7122 | 7.7934 | 7.8746 | 7.9559 | 8.0371 | 8.1183 | 8.1995 | 8.2808 | 8.362
South Australia
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 1.2437 | 1.2231 | 1.2138 | 1.2218 | 1.2065 | 1.2278 | 1.2329 | 1.219 | 1.2175 | 1.2111 | 1.2258 | 1.2357 | 1.2341 | 1.2267 | 1.2202 | 1.2196 | 1.2328 | 1.2448 | 1.2494 | 1.2539 | 1.2539 | 1.2675 | 1.272 | 1.2766 | 1.2811 | 1.2857 | 1.2902 | 1.2947 | 1.2993 | 1.3038
| $500 - $1,000 | 0.87665 | 0.86212 | 0.85559 | 0.86118 | 0.85045 | 0.86545 | 0.86901 | 0.85921 | 0.8582 | 0.85368 | 0.864 | 0.87101 | 0.8699 | 0.86464 | 0.86009 | 0.85964 | 0.86892 | 0.87743 | 0.88063 | 0.88383 | 0.88383 | 0.89342 | 0.89662 | 0.89982 | 0.90301 | 0.90621 | 0.90941 | 0.91261 | 0.9158 | 0.919
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 4.4342 | 4.3607 | 4.3277 | 4.356 | 4.3017 | 4.3776 | 4.3956 | 4.346 | 4.3409 | 4.318 | 4.3702 | 4.4057 | 4.4001 | 4.3735 | 4.3504 | 4.3482 | 4.3951 | 4.4382 | 4.4543 | 4.4705 | 4.4705 | 4.519 | 4.5352 | 4.5514 | 4.5676 | 4.5837 | 4.5999 | 4.6161 | 4.6323 | 4.6484
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 1.2375 | 1.2328 | 1.243 | 1.256 | 1.2556 | 1.2635 | 1.278 | 1.2881 | 1.2988 | 1.2973 | 1.2989 | 1.3166 | 1.3289 | 1.3343 | 1.3449 | 1.3548 | 1.3591 | 1.3694 | 1.3782 | 1.387 | 1.387 | 1.4134 | 1.4221 | 1.4309 | 1.4397 | 1.4485 | 1.4573 | 1.4661 | 1.4748 | 1.4836
| $500 - $1,000 | 0.87226 | 0.86895 | 0.87614 | 0.88531 | 0.88505 | 0.89061 | 0.90079 | 0.90796 | 0.91546 | 0.91445 | 0.91555 | 0.92806 | 0.9367 | 0.94049 | 0.94795 | 0.95496 | 0.958 | 0.96526 | 0.97145 | 0.97765 | 0.97765 | 0.99622 | 1.0024 | 1.0086 | 1.0148 | 1.021 | 1.0272 | 1.0334 | 1.0396 | 1.0458
| $1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| $7,500 - MPC | 4.412 | 4.3953 | 4.4317 | 4.478 | 4.4767 | 4.5048 | 4.5563 | 4.5926 | 4.6305 | 4.6254 | 4.631 | 4.6942 | 4.738 | 4.7571 | 4.7949 | 4.8303 | 4.8457 | 4.8824 | 4.9137 | 4.9451 | 4.9451 | 5.039 | 5.0703 | 5.1017 | 5.133 | 5.1643 | 5.1956 | 5.2269 | 5.2583 | 5.2896
| MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tasmania
| Summer | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 5.5931 | 5.6309 | 5.4322 | 5.431 | 5.4591 | 5.4813 | 5.5189 | 5.5443 | 5.6163 | 5.6581 | 5.7062 | 5.699 | 5.6775 | 5.6812 | 5.7281 | 5.792 | 5.7973 | 5.8427 | 5.8831 | 5.9235 | 5.9235 | 6.0446 | 6.085 | 6.1254 | 6.1658 | 6.2062 | 6.2465 | 6.2869 | 6.3273 | 6.3677
| $500 - $1,000 | 13.3024 | 13.3924 | 12.9199 | 12.917 | 12.9837 | 13.0367 | 13.126 | 13.1864 | 13.3577 | 13.457 | 13.5715 | 13.5544 | 13.5034 | 13.512 | 13.6236 | 13.7756 | 13.7881 | 13.8962 | 13.9923 | 14.0883 | 14.0883 | 14.3764 | 14.4725 | 14.5685 | 14.6646 | 14.7606 | 14.8566 | 14.9527 | 15.0487 | 15.1448
| $1,000 - $7,500 | 0.50388 | 0.50729 | 0.48939 | 0.48928 | 0.49181 | 0.49381 | 0.4972 | 0.49949 | 0.50597 | 0.50973 | 0.51407 | 0.51343 | 0.51149 | 0.51182 | 0.51604 | 0.5218 | 0.52228 | 0.52637 | 0.53001 | 0.53365 | 0.53365 | 0.54456 | 0.5482 | 0.55184 | 0.55548 | 0.55911 | 0.56275 | 0.56639 | 0.57003 | 0.57367
| $7,500 - MPC | 2.3078 | 2.3234 | 2.2414 | 2.2409 | 2.2525 | 2.2617 | 2.2772 | 2.2876 | 2.3174 | 2.3346 | 2.3545 | 2.3515 | 2.3426 | 2.3441 | 2.3635 | 2.3899 | 2.392 | 2.4108 | 2.4274 | 2.4441 | 2.4441 | 2.4941 | 2.5108 | 2.5274 | 2.5441 | 2.5607 | 2.5774 | 2.5941 | 2.6107 | 2.6274
| MPC | 1.6799 | 1.6913 | 1.6316 | 1.6312 | 1.6396 | 1.6463 | 1.6576 | 1.6652 | 1.6869 | 1.6994 | 1.7139 | 1.7117 | 1.7053 | 1.7064 | 1.7204 | 1.7396 | 1.7412 | 1.7549 | 1.767 | 1.7791 | 1.7791 | 1.8155 | 1.8276 | 1.8398 | 1.8519 | 1.864 | 1.8762 | 1.8883 | 1.9004 | 1.9125
| Winter | AEMO Feb 2019 ISP forecast 2020-21: AEMO Feb 2019 ISP forecast; AEMO 2018 ISP forecast 2041-42: AEMO 2018 ISP forecast
| Price band | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| $300 - $500 | 5.6257 | 5.6642 | 5.513 | 5.5163 | 5.5574 | 5.5486 | 5.6025 | 5.6803 | 5.7243 | 5.7848 | 5.7911 | 5.8158 | 5.8311 | 5.8284 | 5.8424 | 5.8915 | 5.9339 | 5.9686 | 6.0036 | 6.0387 | 6.0387 | 6.1439 | 6.1789 | 6.214 | 6.249 | 6.2841 | 6.3191 | 6.3542 | 6.3892 | 6.4243
| $500 - $1,000 | 13.38 | 13.4715 | 13.1121 | 13.1198 | 13.2177 | 13.1967 | 13.3249 | 13.51 | 13.6145 | 13.7585 | 13.7734 | 13.8321 | 13.8685 | 13.8621 | 13.8955 | 14.0121 | 14.113 | 14.1956 | 14.2789 | 14.3623 | 14.3623 | 14.6124 | 14.6958 | 14.7791 | 14.8625 | 14.9459 | 15.0292 | 15.1126 | 15.196 | 15.2793
| $1,000 - $7,500 | 0.50682 | 0.51029 | 0.49667 | 0.49696 | 0.50067 | 0.49988 | 0.50473 | 0.51174 | 0.5157 | 0.52116 | 0.52172 | 0.52394 | 0.52532 | 0.52508 | 0.52635 | 0.53076 | 0.53458 | 0.53771 | 0.54087 | 0.54403 | 0.54403 | 0.5535 | 0.55666 | 0.55982 | 0.56297 | 0.56613 | 0.56929 | 0.57245 | 0.57561 | 0.57876
| $7,500 - MPC | 2.3212 | 2.3371 | 2.2748 | 2.2761 | 2.2931 | 2.2894 | 2.3117 | 2.3438 | 2.3619 | 2.3869 | 2.3895 | 2.3997 | 2.406 | 2.4049 | 2.4107 | 2.4309 | 2.4484 | 2.4627 | 2.4772 | 2.4916 | 2.4916 | 2.535 | 2.5495 | 2.564 | 2.5784 | 2.5929 | 2.6073 | 2.6218 | 2.6363 | 2.6507
| MPC | 1.6897 | 1.7012 | 1.6559 | 1.6568 | 1.6692 | 1.6665 | 1.6827 | 1.7061 | 1.7193 | 1.7375 | 1.7394 | 1.7468 | 1.7514 | 1.7506 | 1.7548 | 1.7695 | 1.7822 | 1.7927 | 1.8032 | 1.8137 | 1.8137 | 1.8453 | 1.8558 | 1.8664 | 1.8769 | 1.8874 | 1.898 | 1.9085 | 1.919 | 1.9295

## Emission Trajectory
TOC
Emissions target trajectories
Primary source: AEMO 2018 ISP Assumptions Workbook v2.3 (no longer available online)
Emissions reduction targets are expressed as a percentage of total emissions across all sectors in 2005. This table includes electricity generation emissions only.
| 28% to 70%: | To be used in Status Quo scenario and Sustained Renewables Uptake scenario
| 52% to 90%: | To be used in Accelerated Transition to a Low Emissions Future scenario
| Financial Year | 28% to 70% Emissions Reduction Target | 52% to 90% Emissions Reduction Target
(Mt CO2-e)
| 2020-21 | 140 | 140
| 2021-22 | 138.7 | 134.4
| 2022-23 | 137.5 | 128.9
| 2023-24 | 136.2 | 123.3
| 2024-25 | 135 | 117.8
| 2025-26 | 133.7 | 112.2
| 2026-27 | 132.4 | 106.7
| 2027-28 | 131.2 | 101.1
| 2028-29 | 129.9 | 95.6
| 2029-30 | 128.6 | 90
| 2030-31 | 127.4 | 84.5
| 2031-32 | 123.6 | 81.1
| 2032-33 | 119.8 | 77.7
| 2033-34 | 116.1 | 74.2
| 2034-35 | 112.3 | 70.8
| 2035-36 | 108.5 | 67.4
| 2036-37 | 104.8 | 64
| 2037-38 | 101 | 60.6
| 2038-39 | 97.2 | 57.2
| 2039-40 | 93.5 | 53.8
| 2040-41 | 89.7 | 50.4
| 2041-42 | 85.9 | 47
| 2042-43 | 82.1 | 43.5
| 2043-44 | 78.4 | 40.1
| 2044-45 | 74.6 | 36.7
| 2045-46 | 70.8 | 33.3
| 2046-47 | 67.1 | 29.9
| 2047-48 | 63.3 | 26.5
| 2048-49 | 59.5 | 23.1
| 2049-50 | 55.7 | 19.7
Emissions reduction targets (including 2030 and 2050 targets) are calculated from 2005 levels, reduced to meet the targeted 2030 and 2050 objectives for each scenario.
The emissions trajectory starts at estimated emissions for 2020-21.

## VRET
TOC
Victorian Renewable Energy Target (VRET)
Primary source: VIC public policy documents
25 % renewable energy generation by 2020, 40 % renewable energy generation by 2025 and 50 % by 2030. Rooftop PV and small non-scheduled PV are assumed to contribute to VRET. For modelling purposes, VRET is demand based.
VRET renewable contribution (GWh)
| Financial year | Percentage of underlying demand | Global Slowdown scenario | Status Quo scenario | Sustained Renewables Uptake scenario | Accelerated Transition scenario
| 2020-21 | 25% | 11695.7218 | 11684.2059 | 11684.2059 | 11840.2213
| 2021-22 | 28.75% | 12946.3814 | 13609.9341 | 13609.9341 | 13833.8888
| 2022-23 | 32.5% | 13914.8477 | 15466.4197 | 15466.4197 | 15929.8352
| 2023-24 | 36.25% | 15232.9608 | 17440.2196 | 17440.2196 | 17946.233
| 2024-25 | 40% | 17038.3486 | 19575.5286 | 19575.5286 | 20295.1492
| 2025-26 | 42% | 17795.3512 | 20614.7928 | 20614.7928 | 21677.8347
| 2026-27 | 44% | 18713.5851 | 21701.8508 | 21701.8508 | 23341.9474
| 2027-28 | 46% | 19834.9858 | 23134.2501 | 23134.2501 | 25143.0443
| 2028-29 | 48% | 20974.9727 | 24578.4735 | 24578.4735 | 27044.8756
| 2029-30 | 50% | 21932.4114 | 26101.7293 | 26101.7293 | 29041.6898

## QRET
TOC
Queensland Renewable Energy Target (QRET)
Primary source: QLD public policy documents
Renewable energy generation is at least 50 % of demand by 2030. Rooftop PV and small non-scheduled PV are assumed to contribute to QRET.
QRET renewable contribution (GWh)
| Financial year | Percentage of underlying demand | Global Slowdown scenario | Status Quo scenario | Sustained Renewables Uptake scenario | Accelerated Transition scenario
| 2020-21 | 0% | 0 | 0 | 0 | 0
| 2021-22 | 5.556% | 2942.889 | 3043.4613 | 3043.4613 | 3145.0802
| 2022-23 | 11.11% | 5923.1134 | 6153.3192 | 6153.3192 | 6354.0489
| 2023-24 | 16.67% | 8845.8443 | 9331.699 | 9331.699 | 9611.406
| 2024-25 | 22.22% | 11752.6681 | 12549.7823 | 12549.7823 | 13046.7639
| 2025-26 | 27.78% | 14543.3326 | 15787.7837 | 15787.7837 | 16493.1804
| 2026-27 | 33.33% | 17430.6681 | 19064.6096 | 19064.6096 | 20157.6669
| 2027-28 | 38.89% | 20313.3802 | 22463.0093 | 22463.0093 | 23863.714
| 2028-29 | 44.44% | 19810.6454 | 25920.476 | 25920.476 | 27661.2154
| 2029-30 | 50% | 22287.482 | 29496.7396 | 29496.7396 | 31582.8328

## Financial assumptions
TOC
Discount Rate
Primary source: AEMO 2019 ISP Assumptions Workbook v1.2
Value represents real, discount rate.
| Asset Class | Discount rate
| Transmission network capital costs | 5.9%
| Generator capital costs | 5.9%
| System | Value of customer reliability (VCR $/MWh)
| VCR (NEM aggregate) | 33460
* This is based on the last NEM wide review of VCR undertaken in 2014 by AEMO.

## Build costs
TOC
Build cost ($/kW) real June 2019 dollars
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Cost to construct new generation, not including connection costs.
| 4 degree scenario: | To be used in Global Slowdown scenario, Status Quo scenario and Sustained Renewables Uptake scenario
| 2 degree scenario: | To be used in Accelerated Transition to a Low Emissions Future scenario
4 degree scenario
| Technology Type | Generator Name | Region | Regional Cost Zone | Cost Scenario | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Large scale Solar PV | Barcaldine | Qld | Qld medium | 4 Degrees | 1247.6066 | 1187.0844 | 1133.9948 | 1092.5849 | 1051.175 | 1016.1358 | 983.2202 | 946.0575 | 913.1419 | 883.4117 | 855.8051 | 840.94 | 821.8277 | 801.6536 | 795.2829 | 765.5527 | 755.9965 | 746.4404 | 740.0696 | 730.5135 | 708.2159 | 686.98 | 667.8677 | 648.7555 | 630.705 | 613.7163 | 605.2219 | 594.604 | 579.7389 | 576.5535
| Large scale Solar PV | Darling Downs | Qld | Qld medium | 4 Degrees | 1247.6066 | 1187.0844 | 1133.9948 | 1092.5849 | 1051.175 | 1016.1358 | 983.2202 | 946.0575 | 913.1419 | 883.4117 | 855.8051 | 840.94 | 821.8277 | 801.6536 | 795.2829 | 765.5527 | 755.9965 | 746.4404 | 740.0696 | 730.5135 | 708.2159 | 686.98 | 667.8677 | 648.7555 | 630.705 | 613.7163 | 605.2219 | 594.604 | 579.7389 | 576.5535
| Large scale Solar PV | Fitzroy | Qld | Qld low | 4 Degrees | 1183.0847 | 1125.6925 | 1075.3484 | 1036.0801 | 996.8118 | 963.5847 | 932.3714 | 897.1306 | 865.9173 | 837.7246 | 811.5457 | 797.4494 | 779.3256 | 760.1948 | 754.1535 | 725.9609 | 716.899 | 707.837 | 701.7957 | 692.7338 | 671.5893 | 651.4517 | 633.3279 | 615.204 | 598.0871 | 581.977 | 573.9219 | 563.8531 | 549.7568 | 546.7361
| Large scale Solar PV | Isaac | Qld | Qld low | 4 Degrees | 1183.0847 | 1125.6925 | 1075.3484 | 1036.0801 | 996.8118 | 963.5847 | 932.3714 | 897.1306 | 865.9173 | 837.7246 | 811.5457 | 797.4494 | 779.3256 | 760.1948 | 754.1535 | 725.9609 | 716.899 | 707.837 | 701.7957 | 692.7338 | 671.5893 | 651.4517 | 633.3279 | 615.204 | 598.0871 | 581.977 | 573.9219 | 563.8531 | 549.7568 | 546.7361
| Large scale Solar PV | North Queensland Clean Energy Hub | Qld | Qld medium | 4 Degrees | 1247.6066 | 1187.0844 | 1133.9948 | 1092.5849 | 1051.175 | 1016.1358 | 983.2202 | 946.0575 | 913.1419 | 883.4117 | 855.8051 | 840.94 | 821.8277 | 801.6536 | 795.2829 | 765.5527 | 755.9965 | 746.4404 | 740.0696 | 730.5135 | 708.2159 | 686.98 | 667.8677 | 648.7555 | 630.705 | 613.7163 | 605.2219 | 594.604 | 579.7389 | 576.5535
| Large scale Solar PV | Northern Queensland | Qld | Qld low | 4 Degrees | 1183.0847 | 1125.6925 | 1075.3484 | 1036.0801 | 996.8118 | 963.5847 | 932.3714 | 897.1306 | 865.9173 | 837.7246 | 811.5457 | 797.4494 | 779.3256 | 760.1948 | 754.1535 | 725.9609 | 716.899 | 707.837 | 701.7957 | 692.7338 | 671.5893 | 651.4517 | 633.3279 | 615.204 | 598.0871 | 581.977 | 573.9219 | 563.8531 | 549.7568 | 546.7361
| Large scale Solar PV | Broken Hill | NSW | NSW high | 4 Degrees | 1310.5819 | 1247.0047 | 1191.2353 | 1147.7351 | 1104.2349 | 1067.4271 | 1032.85 | 993.8114 | 959.2344 | 928.0035 | 899.0034 | 883.3879 | 863.3109 | 842.1186 | 835.4262 | 804.1953 | 794.1568 | 784.1183 | 777.426 | 767.3875 | 743.9643 | 721.6566 | 701.5796 | 681.5026 | 662.541 | 644.6947 | 635.7716 | 624.6177 | 609.0023 | 605.6561
| Large scale Solar PV | Central West New South Wales | NSW | NSW high | 4 Degrees | 1310.5819 | 1247.0047 | 1191.2353 | 1147.7351 | 1104.2349 | 1067.4271 | 1032.85 | 993.8114 | 959.2344 | 928.0035 | 899.0034 | 883.3879 | 863.3109 | 842.1186 | 835.4262 | 804.1953 | 794.1568 | 784.1183 | 777.426 | 767.3875 | 743.9643 | 721.6566 | 701.5796 | 681.5026 | 662.541 | 644.6947 | 635.7716 | 624.6177 | 609.0023 | 605.6561
| Large scale Solar PV | Murray River (NSW) | NSW | NSW high | 4 Degrees | 1310.5819 | 1247.0047 | 1191.2353 | 1147.7351 | 1104.2349 | 1067.4271 | 1032.85 | 993.8114 | 959.2344 | 928.0035 | 899.0034 | 883.3879 | 863.3109 | 842.1186 | 835.4262 | 804.1953 | 794.1568 | 784.1183 | 777.426 | 767.3875 | 743.9643 | 721.6566 | 701.5796 | 681.5026 | 662.541 | 644.6947 | 635.7716 | 624.6177 | 609.0023 | 605.6561
| Large scale Solar PV | North West New South Wales | NSW | NSW medium | 4 Degrees | 1249.9268 | 1189.292 | 1136.1037 | 1094.6167 | 1053.1298 | 1018.0255 | 985.0487 | 947.8168 | 914.84 | 885.0545 | 857.3966 | 842.5038 | 823.356 | 803.1444 | 796.7618 | 766.9763 | 757.4024 | 747.8285 | 741.4459 | 731.872 | 709.5329 | 688.2576 | 669.1097 | 649.9619 | 631.8779 | 614.8576 | 606.3475 | 595.7098 | 580.817 | 577.6257
| Large scale Solar PV | New England | NSW | NSW low | 4 Degrees | 1189.2717 | 1131.5794 | 1080.9721 | 1041.4984 | 1002.0247 | 968.6238 | 937.2473 | 901.8222 | 870.4457 | 842.1056 | 815.7898 | 801.6197 | 783.4011 | 764.1703 | 758.0974 | 729.7574 | 720.648 | 711.5387 | 705.4658 | 696.3565 | 675.1015 | 654.8585 | 636.6399 | 618.4213 | 601.2148 | 585.0205 | 576.9233 | 566.8018 | 552.6318 | 549.5953
| Large scale Solar PV | Riverland (NSW) | NSW | NSW high | 4 Degrees | 1310.5819 | 1247.0047 | 1191.2353 | 1147.7351 | 1104.2349 | 1067.4271 | 1032.85 | 993.8114 | 959.2344 | 928.0035 | 899.0034 | 883.3879 | 863.3109 | 842.1186 | 835.4262 | 804.1953 | 794.1568 | 784.1183 | 777.426 | 767.3875 | 743.9643 | 721.6566 | 701.5796 | 681.5026 | 662.541 | 644.6947 | 635.7716 | 624.6177 | 609.0023 | 605.6561
| Large scale Solar PV | Southern New South Wales Tablelands | NSW | NSW low | 4 Degrees | 1189.2717 | 1131.5794 | 1080.9721 | 1041.4984 | 1002.0247 | 968.6238 | 937.2473 | 901.8222 | 870.4457 | 842.1056 | 815.7898 | 801.6197 | 783.4011 | 764.1703 | 758.0974 | 729.7574 | 720.648 | 711.5387 | 705.4658 | 696.3565 | 675.1015 | 654.8585 | 636.6399 | 618.4213 | 601.2148 | 585.0205 | 576.9233 | 566.8018 | 552.6318 | 549.5953
| Large scale Solar PV | Murray River | NSW | NSW high | 4 Degrees | 1310.5819 | 1247.0047 | 1191.2353 | 1147.7351 | 1104.2349 | 1067.4271 | 1032.85 | 993.8114 | 959.2344 | 928.0035 | 899.0034 | 883.3879 | 863.3109 | 842.1186 | 835.4262 | 804.1953 | 794.1568 | 784.1183 | 777.426 | 767.3875 | 743.9643 | 721.6566 | 701.5796 | 681.5026 | 662.541 | 644.6947 | 635.7716 | 624.6177 | 609.0023 | 605.6561
| Large scale Solar PV | Eastern Eyre Peninsula | SA | SA medium | 4 Degrees | 1239.8728 | 1179.7258 | 1126.9653 | 1085.812 | 1044.6588 | 1009.8369 | 977.1253 | 940.1929 | 907.4814 | 877.9355 | 850.5 | 835.7271 | 816.7333 | 796.6843 | 790.353 | 760.8071 | 751.3102 | 741.8133 | 735.482 | 725.9851 | 703.8257 | 682.7215 | 663.7277 | 644.7339 | 626.7953 | 609.9119 | 601.4702 | 590.9181 | 576.1452 | 572.9795
| Large scale Solar PV | Leigh Creek | SA | SA medium | 4 Degrees | 1239.8728 | 1179.7258 | 1126.9653 | 1085.812 | 1044.6588 | 1009.8369 | 977.1253 | 940.1929 | 907.4814 | 877.9355 | 850.5 | 835.7271 | 816.7333 | 796.6843 | 790.353 | 760.8071 | 751.3102 | 741.8133 | 735.482 | 725.9851 | 703.8257 | 682.7215 | 663.7277 | 644.7339 | 626.7953 | 609.9119 | 601.4702 | 590.9181 | 576.1452 | 572.9795
| Large scale Solar PV | Northern South Australia | SA | SA medium | 4 Degrees | 1239.8728 | 1179.7258 | 1126.9653 | 1085.812 | 1044.6588 | 1009.8369 | 977.1253 | 940.1929 | 907.4814 | 877.9355 | 850.5 | 835.7271 | 816.7333 | 796.6843 | 790.353 | 760.8071 | 751.3102 | 741.8133 | 735.482 | 725.9851 | 703.8257 | 682.7215 | 663.7277 | 644.7339 | 626.7953 | 609.9119 | 601.4702 | 590.9181 | 576.1452 | 572.9795
| Large scale Solar PV | Riverland (SA) | SA | SA medium | 4 Degrees | 1239.8728 | 1179.7258 | 1126.9653 | 1085.812 | 1044.6588 | 1009.8369 | 977.1253 | 940.1929 | 907.4814 | 877.9355 | 850.5 | 835.7271 | 816.7333 | 796.6843 | 790.353 | 760.8071 | 751.3102 | 741.8133 | 735.482 | 725.9851 | 703.8257 | 682.7215 | 663.7277 | 644.7339 | 626.7953 | 609.9119 | 601.4702 | 590.9181 | 576.1452 | 572.9795
| Large scale Solar PV | Roxby Downs | SA | SA medium | 4 Degrees | 1239.8728 | 1179.7258 | 1126.9653 | 1085.812 | 1044.6588 | 1009.8369 | 977.1253 | 940.1929 | 907.4814 | 877.9355 | 850.5 | 835.7271 | 816.7333 | 796.6843 | 790.353 | 760.8071 | 751.3102 | 741.8133 | 735.482 | 725.9851 | 703.8257 | 682.7215 | 663.7277 | 644.7339 | 626.7953 | 609.9119 | 601.4702 | 590.9181 | 576.1452 | 572.9795
| Large scale Solar PV | Western Eyre Peninsula | SA | SA medium | 4 Degrees | 1239.8728 | 1179.7258 | 1126.9653 | 1085.812 | 1044.6588 | 1009.8369 | 977.1253 | 940.1929 | 907.4814 | 877.9355 | 850.5 | 835.7271 | 816.7333 | 796.6843 | 790.353 | 760.8071 | 751.3102 | 741.8133 | 735.482 | 725.9851 | 703.8257 | 682.7215 | 663.7277 | 644.7339 | 626.7953 | 609.9119 | 601.4702 | 590.9181 | 576.1452 | 572.9795
| Wind | Barcaldine | Qld | Qld medium | 4 Degrees | 1966.7375 | 1947.9298 | 1931.2715 | 1914.762 | 1900.3624 | 1886.0902 | 1874.8626 | 1863.7335 | 1852.7016 | 1841.7656 | 1830.9243 | 1819.2245 | 1795.3025 | 1764.9782 | 1754.6481 | 1744.4057 | 1734.2496 | 1724.1789 | 1714.1925 | 1703.3691 | 1693.5519 | 1683.8158 | 1675.0688 | 1665.4883 | 1656.8874 | 1648.3565 | 1639.0005 | 1628.8294 | 1618.74 | 1607.8479
| Wind | Darling Downs | Qld | Qld low | 4 Degrees | 1847.1149 | 1829.451 | 1813.806 | 1798.3006 | 1784.7768 | 1771.3727 | 1760.828 | 1750.3758 | 1740.0149 | 1729.7441 | 1719.5622 | 1708.574 | 1686.107 | 1657.6271 | 1647.9254 | 1638.3059 | 1628.7675 | 1619.3094 | 1609.9304 | 1599.7652 | 1590.5452 | 1581.4013 | 1573.1862 | 1564.1885 | 1556.1107 | 1548.0987 | 1539.3118 | 1529.7593 | 1520.2836 | 1510.0539
| Wind | Fitzroy | Qld | Qld low | 4 Degrees | 1847.1149 | 1829.451 | 1813.806 | 1798.3006 | 1784.7768 | 1771.3727 | 1760.828 | 1750.3758 | 1740.0149 | 1729.7441 | 1719.5622 | 1708.574 | 1686.107 | 1657.6271 | 1647.9254 | 1638.3059 | 1628.7675 | 1619.3094 | 1609.9304 | 1599.7652 | 1590.5452 | 1581.4013 | 1573.1862 | 1564.1885 | 1556.1107 | 1548.0987 | 1539.3118 | 1529.7593 | 1520.2836 | 1510.0539
| Wind | Isaac | Qld | Qld low | 4 Degrees | 1847.1149 | 1829.451 | 1813.806 | 1798.3006 | 1784.7768 | 1771.3727 | 1760.828 | 1750.3758 | 1740.0149 | 1729.7441 | 1719.5622 | 1708.574 | 1686.107 | 1657.6271 | 1647.9254 | 1638.3059 | 1628.7675 | 1619.3094 | 1609.9304 | 1599.7652 | 1590.5452 | 1581.4013 | 1573.1862 | 1564.1885 | 1556.1107 | 1548.0987 | 1539.3118 | 1529.7593 | 1520.2836 | 1510.0539
| Wind | North Queensland Clean Energy Hub | Qld | Qld medium | 4 Degrees | 1966.7375 | 1947.9298 | 1931.2715 | 1914.762 | 1900.3624 | 1886.0902 | 1874.8626 | 1863.7335 | 1852.7016 | 1841.7656 | 1830.9243 | 1819.2245 | 1795.3025 | 1764.9782 | 1754.6481 | 1744.4057 | 1734.2496 | 1724.1789 | 1714.1925 | 1703.3691 | 1693.5519 | 1683.8158 | 1675.0688 | 1665.4883 | 1656.8874 | 1648.3565 | 1639.0005 | 1628.8294 | 1618.74 | 1607.8479
| Wind | Broken Hill | NSW | NSW high | 4 Degrees | 2081.0827 | 2061.1815 | 2043.5547 | 2026.0853 | 2010.8485 | 1995.7466 | 1983.8662 | 1972.0901 | 1960.4168 | 1948.845 | 1937.3734 | 1924.9933 | 1899.6806 | 1867.5932 | 1856.6626 | 1845.8246 | 1835.0781 | 1824.4219 | 1813.8549 | 1802.4022 | 1792.0142 | 1781.7121 | 1772.4565 | 1762.319 | 1753.2181 | 1744.1912 | 1734.2913 | 1723.5288 | 1712.8528 | 1701.3274
| Wind | Central West New South Wales | NSW | NSW high | 4 Degrees | 2081.0827 | 2061.1815 | 2043.5547 | 2026.0853 | 2010.8485 | 1995.7466 | 1983.8662 | 1972.0901 | 1960.4168 | 1948.845 | 1937.3734 | 1924.9933 | 1899.6806 | 1867.5932 | 1856.6626 | 1845.8246 | 1835.0781 | 1824.4219 | 1813.8549 | 1802.4022 | 1792.0142 | 1781.7121 | 1772.4565 | 1762.319 | 1753.2181 | 1744.1912 | 1734.2913 | 1723.5288 | 1712.8528 | 1701.3274
| Wind | Murray River (NSW) | Vic | NSW high | 4 Degrees | 1908.6853 | 1890.4327 | 1874.2662 | 1858.2439 | 1844.2694 | 1830.4185 | 1819.5223 | 1808.7217 | 1798.0154 | 1787.4022 | 1776.8809 | 1765.5264 | 1742.3106 | 1712.8813 | 1702.8562 | 1692.9161 | 1683.0598 | 1673.2864 | 1663.5947 | 1653.0908 | 1643.5633 | 1634.1147 | 1625.6258 | 1616.3281 | 1607.9811 | 1599.702 | 1590.6222 | 1580.7513 | 1570.9597 | 1560.3891
| Wind | North West New South Wales | NSW | NSW medium | 4 Degrees | 1974.6537 | 1955.7703 | 1939.045 | 1922.469 | 1908.0114 | 1893.6818 | 1882.409 | 1871.2351 | 1860.1588 | 1849.1788 | 1838.2938 | 1826.5469 | 1802.5287 | 1772.0823 | 1761.7107 | 1751.427 | 1741.2301 | 1731.1188 | 1721.0922 | 1710.2252 | 1700.3685 | 1690.5933 | 1681.811 | 1672.1919 | 1663.5565 | 1654.9912 | 1645.5976 | 1635.3855 | 1625.2555 | 1614.3196
| Wind | New England | NSW | NSW low | 4 Degrees | 1868.2247 | 1850.3591 | 1834.5352 | 1818.8526 | 1805.1743 | 1791.617 | 1780.9518 | 1770.3801 | 1759.9008 | 1749.5126 | 1739.2143 | 1728.1005 | 1705.3768 | 1676.5714 | 1666.7588 | 1657.0294 | 1647.382 | 1637.8158 | 1628.3296 | 1618.0483 | 1608.7228 | 1599.4744 | 1591.1655 | 1582.0649 | 1573.8949 | 1565.7913 | 1556.9039 | 1547.2423 | 1537.6582 | 1527.3117
| Wind | Riverland (NSW) | NSW | NSW high | 4 Degrees | 2081.0827 | 2061.1815 | 2043.5547 | 2026.0853 | 2010.8485 | 1995.7466 | 1983.8662 | 1972.0901 | 1960.4168 | 1948.845 | 1937.3734 | 1924.9933 | 1899.6806 | 1867.5932 | 1856.6626 | 1845.8246 | 1835.0781 | 1824.4219 | 1813.8549 | 1802.4022 | 1792.0142 | 1781.7121 | 1772.4565 | 1762.319 | 1753.2181 | 1744.1912 | 1734.2913 | 1723.5288 | 1712.8528 | 1701.3274
| Wind | Southern New South Wales Tablelands | NSW | NSW low | 4 Degrees | 1868.2247 | 1850.3591 | 1834.5352 | 1818.8526 | 1805.1743 | 1791.617 | 1780.9518 | 1770.3801 | 1759.9008 | 1749.5126 | 1739.2143 | 1728.1005 | 1705.3768 | 1676.5714 | 1666.7588 | 1657.0294 | 1647.382 | 1637.8158 | 1628.3296 | 1618.0483 | 1608.7228 | 1599.4744 | 1591.1655 | 1582.0649 | 1573.8949 | 1565.7913 | 1556.9039 | 1547.2423 | 1537.6582 | 1527.3117
| Wind | Gippsland | Vic | Vic medium | 4 Degrees | 1873.5022 | 1855.5861 | 1839.7175 | 1823.9906 | 1810.2736 | 1796.678 | 1785.9827 | 1775.3812 | 1764.8722 | 1754.4547 | 1744.1273 | 1732.9822 | 1710.1943 | 1681.3075 | 1671.4671 | 1661.7102 | 1652.0357 | 1642.4424 | 1632.9294 | 1622.619 | 1613.2672 | 1603.9927 | 1595.6603 | 1586.534 | 1578.3409 | 1570.2144 | 1561.3019 | 1551.613 | 1542.0019 | 1531.6261
| Wind | Moyne | Vic | Vic medium | 4 Degrees | 1873.5022 | 1855.5861 | 1839.7175 | 1823.9906 | 1810.2736 | 1796.678 | 1785.9827 | 1775.3812 | 1764.8722 | 1754.4547 | 1744.1273 | 1732.9822 | 1710.1943 | 1681.3075 | 1671.4671 | 1661.7102 | 1652.0357 | 1642.4424 | 1632.9294 | 1622.619 | 1613.2672 | 1603.9927 | 1595.6603 | 1586.534 | 1578.3409 | 1570.2144 | 1561.3019 | 1551.613 | 1542.0019 | 1531.6261
| Wind | Murray River | Vic | Vic high | 4 Degrees | 1908.6853 | 1890.4327 | 1874.2662 | 1858.2439 | 1844.2694 | 1830.4185 | 1819.5223 | 1808.7217 | 1798.0154 | 1787.4022 | 1776.8809 | 1765.5264 | 1742.3106 | 1712.8813 | 1702.8562 | 1692.9161 | 1683.0598 | 1673.2864 | 1663.5947 | 1653.0908 | 1643.5633 | 1634.1147 | 1625.6258 | 1616.3281 | 1607.9811 | 1599.702 | 1590.6222 | 1580.7513 | 1570.9597 | 1560.3891
| Wind | Western Victoria | Vic | Vic high | 4 Degrees | 1908.6853 | 1890.4327 | 1874.2662 | 1858.2439 | 1844.2694 | 1830.4185 | 1819.5223 | 1808.7217 | 1798.0154 | 1787.4022 | 1776.8809 | 1765.5264 | 1742.3106 | 1712.8813 | 1702.8562 | 1692.9161 | 1683.0598 | 1673.2864 | 1663.5947 | 1653.0908 | 1643.5633 | 1634.1147 | 1625.6258 | 1616.3281 | 1607.9811 | 1599.702 | 1590.6222 | 1580.7513 | 1570.9597 | 1560.3891
| Wind | Eastern Eyre Peninsula | SA | SA medium | 4 Degrees | 1940.3502 | 1921.7948 | 1905.36 | 1889.072 | 1874.8655 | 1860.7849 | 1849.7079 | 1838.7281 | 1827.8442 | 1817.0549 | 1806.3591 | 1794.8163 | 1771.2153 | 1741.2978 | 1731.1063 | 1721.0013 | 1710.9815 | 1701.046 | 1691.1935 | 1680.5153 | 1670.8298 | 1661.2244 | 1652.5947 | 1643.1427 | 1634.6573 | 1626.2408 | 1617.0104 | 1606.9757 | 1597.0217 | 1586.2757
| Wind | Leigh Creek | SA | SA medium | 4 Degrees | 1940.3502 | 1921.7948 | 1905.36 | 1889.072 | 1874.8655 | 1860.7849 | 1849.7079 | 1838.7281 | 1827.8442 | 1817.0549 | 1806.3591 | 1794.8163 | 1771.2153 | 1741.2978 | 1731.1063 | 1721.0013 | 1710.9815 | 1701.046 | 1691.1935 | 1680.5153 | 1670.8298 | 1661.2244 | 1652.5947 | 1643.1427 | 1634.6573 | 1626.2408 | 1617.0104 | 1606.9757 | 1597.0217 | 1586.2757
| Wind | Mid-North South Australia | SA | SA Low | 4 Degrees | 1826.005 | 1808.543 | 1793.0768 | 1777.7486 | 1764.3794 | 1751.1285 | 1740.7043 | 1730.3715 | 1720.129 | 1709.9756 | 1699.91 | 1689.0474 | 1666.8372 | 1638.6828 | 1629.0919 | 1619.5824 | 1610.1531 | 1600.803 | 1591.5312 | 1581.4822 | 1572.3675 | 1563.3281 | 1555.207 | 1546.312 | 1538.3266 | 1530.4062 | 1521.7196 | 1512.2763 | 1502.9089 | 1492.7962
| Wind | Northern South Australia | SA | SA medium | 4 Degrees | 1940.3502 | 1921.7948 | 1905.36 | 1889.072 | 1874.8655 | 1860.7849 | 1849.7079 | 1838.7281 | 1827.8442 | 1817.0549 | 1806.3591 | 1794.8163 | 1771.2153 | 1741.2978 | 1731.1063 | 1721.0013 | 1710.9815 | 1701.046 | 1691.1935 | 1680.5153 | 1670.8298 | 1661.2244 | 1652.5947 | 1643.1427 | 1634.6573 | 1626.2408 | 1617.0104 | 1606.9757 | 1597.0217 | 1586.2757
| Wind | Riverland (SA) | SA | SA Low | 4 Degrees | 1826.005 | 1808.543 | 1793.0768 | 1777.7486 | 1764.3794 | 1751.1285 | 1740.7043 | 1730.3715 | 1720.129 | 1709.9756 | 1699.91 | 1689.0474 | 1666.8372 | 1638.6828 | 1629.0919 | 1619.5824 | 1610.1531 | 1600.803 | 1591.5312 | 1581.4822 | 1572.3675 | 1563.3281 | 1555.207 | 1546.312 | 1538.3266 | 1530.4062 | 1521.7196 | 1512.2763 | 1502.9089 | 1492.7962
| Wind | South East South Australia | SA | SA medium | 4 Degrees | 1940.3502 | 1921.7948 | 1905.36 | 1889.072 | 1874.8655 | 1860.7849 | 1849.7079 | 1838.7281 | 1827.8442 | 1817.0549 | 1806.3591 | 1794.8163 | 1771.2153 | 1741.2978 | 1731.1063 | 1721.0013 | 1710.9815 | 1701.046 | 1691.1935 | 1680.5153 | 1670.8298 | 1661.2244 | 1652.5947 | 1643.1427 | 1634.6573 | 1626.2408 | 1617.0104 | 1606.9757 | 1597.0217 | 1586.2757
| Wind | Western Eyre Peninsula | SA | SA medium | 4 Degrees | 1940.3502 | 1921.7948 | 1905.36 | 1889.072 | 1874.8655 | 1860.7849 | 1849.7079 | 1838.7281 | 1827.8442 | 1817.0549 | 1806.3591 | 1794.8163 | 1771.2153 | 1741.2978 | 1731.1063 | 1721.0013 | 1710.9815 | 1701.046 | 1691.1935 | 1680.5153 | 1670.8298 | 1661.2244 | 1652.5947 | 1643.1427 | 1634.6573 | 1626.2408 | 1617.0104 | 1606.9757 | 1597.0217 | 1586.2757
| Wind | Yorke Peninsula | SA | SA Low | 4 Degrees | 1826.005 | 1808.543 | 1793.0768 | 1777.7486 | 1764.3794 | 1751.1285 | 1740.7043 | 1730.3715 | 1720.129 | 1709.9756 | 1699.91 | 1689.0474 | 1666.8372 | 1638.6828 | 1629.0919 | 1619.5824 | 1610.1531 | 1600.803 | 1591.5312 | 1581.4822 | 1572.3675 | 1563.3281 | 1555.207 | 1546.312 | 1538.3266 | 1530.4062 | 1521.7196 | 1512.2763 | 1502.9089 | 1492.7962
| Wind | North East Tasmania | Tas | Tas high | 4 Degrees | 2046.7792 | 2027.206 | 2009.8698 | 1992.6883 | 1977.7027 | 1962.8497 | 1951.1651 | 1939.5831 | 1928.1022 | 1916.7212 | 1905.4386 | 1893.2627 | 1868.3671 | 1836.8087 | 1826.0582 | 1815.3989 | 1804.8296 | 1794.349 | 1783.9562 | 1772.6922 | 1762.4755 | 1752.3432 | 1743.2402 | 1733.2698 | 1724.3189 | 1715.4408 | 1705.704 | 1695.119 | 1684.619 | 1673.2836
| Wind | North West Tasmania | Tas | Tas medium | 4 Degrees | 1942.9889 | 1924.4083 | 1907.9511 | 1891.641 | 1877.4152 | 1863.3154 | 1852.2234 | 1841.2286 | 1830.3299 | 1819.526 | 1808.8156 | 1797.2571 | 1773.624 | 1743.6658 | 1733.4605 | 1723.3417 | 1713.3083 | 1703.3593 | 1693.4934 | 1682.8007 | 1673.102 | 1663.4835 | 1654.8421 | 1645.3773 | 1636.8803 | 1628.4524 | 1619.2094 | 1609.1611 | 1599.1935 | 1588.4329
| Wind | Tasmania Midlands | Tas | Tas medium | 4 Degrees | 1942.9889 | 1924.4083 | 1907.9511 | 1891.641 | 1877.4152 | 1863.3154 | 1852.2234 | 1841.2286 | 1830.3299 | 1819.526 | 1808.8156 | 1797.2571 | 1773.624 | 1743.6658 | 1733.4605 | 1723.3417 | 1713.3083 | 1703.3593 | 1693.4934 | 1682.8007 | 1673.102 | 1663.4835 | 1654.8421 | 1645.3773 | 1636.8803 | 1628.4524 | 1619.2094 | 1609.1611 | 1599.1935 | 1588.4329
| OCGT | OCGT | QLD | Qld low | 4 Degrees | 895.7191 | 894.7127 | 892.6998 | 891.6934 | 889.6805 | 888.6741 | 886.6613 | 885.6548 | 884.6484 | 882.6356 | 881.6291 | 879.6163 | 878.6099 | 877.6034 | 875.5906 | 874.5842 | 872.5713 | 871.5649 | 870.5585 | 868.5456 | 867.5392 | 866.5328 | 864.5199 | 863.5135 | 861.5006 | 860.4942 | 859.4878 | 857.4749 | 856.4685 | 855.4621
| OCGT | OCGT | NSW | NSW low | 4 Degrees | 899.9709 | 898.9597 | 896.9373 | 895.9261 | 893.9037 | 892.8925 | 890.8701 | 889.8589 | 888.8477 | 886.8252 | 885.814 | 883.7916 | 882.7804 | 881.7692 | 879.7468 | 878.7356 | 876.7132 | 875.702 | 874.6908 | 872.6684 | 871.6572 | 870.646 | 868.6236 | 867.6124 | 865.59 | 864.5788 | 863.5676 | 861.5452 | 860.534 | 859.5228
| OCGT | OCGT | SA | SA low | 4 Degrees | 891.4673 | 890.4657 | 888.4624 | 887.4607 | 885.4574 | 884.4558 | 882.4525 | 881.4508 | 880.4492 | 878.4459 | 877.4442 | 875.4409 | 874.4393 | 873.4376 | 871.4343 | 870.4327 | 868.4294 | 867.4278 | 866.4261 | 864.4228 | 863.4212 | 862.4195 | 860.4162 | 859.4146 | 857.4113 | 856.4096 | 855.408 | 853.4047 | 852.403 | 851.4014
| OCGT | OCGT | Tas | Tas low | 4 Degrees | 894.1253 | 893.1207 | 891.1114 | 890.1068 | 888.0975 | 887.0929 | 885.0836 | 884.079 | 883.0743 | 881.0651 | 880.0604 | 878.0512 | 877.0465 | 876.0419 | 874.0326 | 873.028 | 871.0187 | 870.0141 | 869.0094 | 867.0002 | 865.9955 | 864.9909 | 862.9816 | 861.977 | 859.9677 | 858.9631 | 857.9585 | 855.9492 | 854.9445 | 853.9399
| OCGT | OCGT | Vic | Vic low | 4 Degrees | 890.4044 | 889.4039 | 887.403 | 886.4026 | 884.4016 | 883.4012 | 881.4003 | 880.3998 | 879.3994 | 877.3985 | 876.398 | 874.3971 | 873.3967 | 872.3962 | 870.3953 | 869.3948 | 867.3939 | 866.3935 | 865.393 | 863.3921 | 862.3917 | 861.3912 | 859.3903 | 858.3898 | 856.3889 | 855.3885 | 854.388 | 852.3871 | 851.3867 | 850.3862
| CCGT | CCGT | QLD | Qld low | 4 Degrees | 1280.5669 | 1278.5534 | 1276.54 | 1274.5265 | 1272.513 | 1270.4996 | 1268.4861 | 1266.4726 | 1264.4592 | 1262.4457 | 1260.4322 | 1258.4187 | 1256.4053 | 1254.3918 | 1252.3783 | 1250.3649 | 1248.3514 | 1246.3379 | 1244.3245 | 1242.311 | 1240.2975 | 1238.284 | 1236.2706 | 1234.2571 | 1232.2436 | 1230.2302 | 1228.2167 | 1226.2032 | 1224.1898 | 1222.1763
| CCGT | CCGT | NSW | NSW low | 4 Degrees | 1287.3575 | 1285.3334 | 1283.3092 | 1281.2851 | 1279.261 | 1277.2368 | 1275.2127 | 1273.1885 | 1271.1644 | 1269.1402 | 1267.1161 | 1265.0919 | 1263.0678 | 1261.0436 | 1259.0195 | 1256.9953 | 1254.9712 | 1252.947 | 1250.9229 | 1248.8987 | 1246.8746 | 1244.8505 | 1242.8263 | 1240.8022 | 1238.778 | 1236.7539 | 1234.7297 | 1232.7056 | 1230.6814 | 1228.6573
| CCGT | CCGT | SA | SA low | 4 Degrees | 1273.7763 | 1271.7735 | 1269.7707 | 1267.7679 | 1265.7651 | 1263.7623 | 1261.7595 | 1259.7567 | 1257.7539 | 1255.7511 | 1253.7484 | 1251.7456 | 1249.7428 | 1247.74 | 1245.7372 | 1243.7344 | 1241.7316 | 1239.7288 | 1237.726 | 1235.7232 | 1233.7204 | 1231.7176 | 1229.7148 | 1227.712 | 1225.7093 | 1223.7065 | 1221.7037 | 1219.7009 | 1217.6981 | 1215.6953
| CCGT | CCGT | Tas | Tas low | 4 Degrees | 1278.0211 | 1276.0116 | 1274.0022 | 1271.9927 | 1269.9832 | 1267.9738 | 1265.9643 | 1263.9548 | 1261.9454 | 1259.9359 | 1257.9264 | 1255.917 | 1253.9075 | 1251.898 | 1249.8886 | 1247.8791 | 1245.8696 | 1243.8602 | 1241.8507 | 1239.8412 | 1237.8318 | 1235.8223 | 1233.8128 | 1231.8034 | 1229.7939 | 1227.7844 | 1225.775 | 1223.7655 | 1221.756 | 1219.7466
| CCGT | CCGT | Vic | Vic low | 4 Degrees | 1272.0786 | 1270.0785 | 1268.0784 | 1266.0783 | 1264.0781 | 1262.078 | 1260.0779 | 1258.0778 | 1256.0776 | 1254.0775 | 1252.0774 | 1250.0773 | 1248.0771 | 1246.077 | 1244.0769 | 1242.0768 | 1240.0766 | 1238.0765 | 1236.0764 | 1234.0763 | 1232.0762 | 1230.076 | 1228.0759 | 1226.0758 | 1224.0757 | 1222.0755 | 1220.0754 | 1218.0753 | 1216.0752 | 1214.075
| Battery storage 2hrs | Battery storage 2hrs | QLD | Qld low | 4 Degrees | 1363.3023 | 1305.9001 | 1250.548 | 1193.1458 | 1127.5433 | 1074.2412 | 1035.2897 | 1010.6888 | 996.3382 | 959.4368 | 959.4368 | 959.4368 | 957.3868 | 957.3868 | 957.3868 | 955.3367 | 955.3367 | 955.3367 | 943.0362 | 926.6356 | 926.6356 | 926.6356 | 926.6356 | 926.6356 | 926.6356 | 924.5855 | 924.5855 | 924.5855 | 924.5855 | 924.5855
| Battery storage 2hrs | Battery storage 2hrs | NSW | NSW low | 4 Degrees | 1389.9442 | 1331.4202 | 1274.9864 | 1216.4624 | 1149.5779 | 1095.2342 | 1055.5215 | 1030.4398 | 1015.8088 | 978.1863 | 978.1863 | 978.1863 | 976.0962 | 976.0962 | 976.0962 | 974.006 | 974.006 | 974.006 | 961.4652 | 944.744 | 944.744 | 944.744 | 944.744 | 944.744 | 944.744 | 942.6539 | 942.6539 | 942.6539 | 942.6539 | 942.6539
| Battery storage 2hrs | Battery storage 2hrs | SA | SA low | 4 Degrees | 1336.6605 | 1280.38 | 1226.1096 | 1169.8292 | 1105.5087 | 1053.2482 | 1015.0579 | 990.9378 | 976.8676 | 940.6874 | 940.6874 | 940.6874 | 938.6774 | 938.6774 | 938.6774 | 936.6673 | 936.6673 | 936.6673 | 924.6072 | 908.5271 | 908.5271 | 908.5271 | 908.5271 | 908.5271 | 908.5271 | 906.5171 | 906.5171 | 906.5171 | 906.5171 | 906.5171
| Battery storage 2hrs | Battery storage 2hrs | Tas | Tas low | 4 Degrees | 1353.3116 | 1296.3301 | 1241.3836 | 1184.4021 | 1119.2803 | 1066.3689 | 1027.7028 | 1003.2822 | 989.0368 | 952.4058 | 952.4058 | 952.4058 | 950.3707 | 950.3707 | 950.3707 | 948.3357 | 948.3357 | 948.3357 | 936.1253 | 919.8449 | 919.8449 | 919.8449 | 919.8449 | 919.8449 | 919.8449 | 917.8098 | 917.8098 | 917.8098 | 917.8098 | 917.8098
| Battery storage 2hrs | Battery storage 2hrs | Vic | Vic low | 4 Degrees | 1330 | 1274 | 1220 | 1164 | 1100 | 1048 | 1010 | 986 | 972 | 936 | 936 | 936 | 934 | 934 | 934 | 932 | 932 | 932 | 920 | 904 | 904 | 904 | 904 | 904 | 904 | 902 | 902 | 902 | 902 | 902
| Pumped hydro 6 hrs | Pumped hydro 6 hrs | NSW | NSW | 4 Degrees | 1571.5725 | 1568.9423 | 1567.6272 | 1564.9969 | 1563.6818 | 1561.0515 | 1558.4213 | 1557.1062 | 1554.4759 | 1551.8457 | 1550.5306 | 1547.9003 | 1546.5852 | 1543.9549 | 1541.3247 | 1540.0096 | 1537.3793 | 1536.0642 | 1533.434 | 1530.8037 | 1529.4886 | 1526.8583 | 1525.5432 | 1522.913 | 1520.2827 | 1518.9676 | 1516.3373 | 1515.0222 | 1512.392 | 1511.0769
| Pumped hydro 6 hrs | Pumped hydro 6 hrs | QLD | QLD | 4 Degrees | 1523.625 | 1521.075 | 1519.8 | 1517.25 | 1515.975 | 1513.425 | 1510.875 | 1509.6 | 1507.05 | 1504.5 | 1503.225 | 1500.675 | 1499.4 | 1496.85 | 1494.3 | 1493.025 | 1490.475 | 1489.2 | 1486.65 | 1484.1 | 1482.825 | 1480.275 | 1479 | 1476.45 | 1473.9 | 1472.625 | 1470.075 | 1468.8 | 1466.25 | 1464.975
| Pumped hydro 6 hrs | Pumped hydro 6 hrs | SA | SA | 4 Degrees | 1921.9583 | 1918.7417 | 1917.1333 | 1913.9167 | 1912.3083 | 1909.0917 | 1905.875 | 1904.2667 | 1901.05 | 1897.8333 | 1896.225 | 1893.0083 | 1891.4 | 1888.1833 | 1884.9667 | 1883.3583 | 1880.1417 | 1878.5333 | 1875.3167 | 1872.1 | 1870.4917 | 1867.275 | 1865.6667 | 1862.45 | 1859.2333 | 1857.625 | 1854.4083 | 1852.8 | 1849.5833 | 1847.975
| Pumped hydro 6 hrs | Pumped hydro 6 hrs | Tas | Tas | 4 Degrees | 1155.1667 | 1153.2333 | 1152.2667 | 1150.3333 | 1149.3667 | 1147.4333 | 1145.5 | 1144.5333 | 1142.6 | 1140.6667 | 1139.7 | 1137.7667 | 1136.8 | 1134.8667 | 1132.9333 | 1131.9667 | 1130.0333 | 1129.0667 | 1127.1333 | 1125.2 | 1124.2333 | 1122.3 | 1121.3333 | 1119.4 | 1117.4667 | 1116.5 | 1114.5667 | 1113.6 | 1111.6667 | 1110.7
| Pumped hydro 6 hrs | Pumped hydro 6 hrs | Vic | Vic | 4 Degrees | 1523.625 | 1521.075 | 1519.8 | 1517.25 | 1515.975 | 1513.425 | 1510.875 | 1509.6 | 1507.05 | 1504.5 | 1503.225 | 1500.675 | 1499.4 | 1496.85 | 1494.3 | 1493.025 | 1490.475 | 1489.2 | 1486.65 | 1484.1 | 1482.825 | 1480.275 | 1479 | 1476.45 | 1473.9 | 1472.625 | 1470.075 | 1468.8 | 1466.25 | 1464.975
| Pumped hydro 24 hrs | Pumped hydro 24 hrs | NSW | NSW | 4 Degrees | 2109.8389 | 2106.3078 | 2104.5422 | 2101.0111 | 2099.2456 | 2095.7144 | 2092.1833 | 2090.4178 | 2086.8867 | 2083.3556 | 2081.59 | 2078.0589 | 2076.2933 | 2072.7622 | 2069.2311 | 2067.4656 | 2063.9344 | 2062.1689 | 2058.6378 | 2055.1067 | 2053.3411 | 2049.81 | 2048.0444 | 2044.5133 | 2040.9822 | 2039.2167 | 2035.6856 | 2033.92 | 2030.3889 | 2028.6233
| Pumped hydro 24 hrs | Pumped hydro 24 hrs | QLD | QLD | 4 Degrees | 2074.9545 | 2071.4818 | 2069.7455 | 2066.2727 | 2064.5364 | 2061.0636 | 2057.5909 | 2055.8545 | 2052.3818 | 2048.9091 | 2047.1727 | 2043.7 | 2041.9636 | 2038.4909 | 2035.0182 | 2033.2818 | 2029.8091 | 2028.0727 | 2024.6 | 2021.1273 | 2019.3909 | 2015.9182 | 2014.1818 | 2010.7091 | 2007.2364 | 2005.5 | 2002.0273 | 2000.2909 | 1996.8182 | 1995.0818
| Pumped hydro 24 hrs | Pumped hydro 24 hrs | SA | SA | 4 Degrees | 3734.375 | 3728.125 | 3725 | 3718.75 | 3715.625 | 3709.375 | 3703.125 | 3700 | 3693.75 | 3687.5 | 3684.375 | 3678.125 | 3675 | 3668.75 | 3662.5 | 3659.375 | 3653.125 | 3650 | 3643.75 | 3637.5 | 3634.375 | 3628.125 | 3625 | 3618.75 | 3612.5 | 3609.375 | 3603.125 | 3600 | 3593.75 | 3590.625
| Pumped hydro 24 hrs | Pumped hydro 24 hrs | Tas | Tas | 4 Degrees | 1384.2083 | 1381.8917 | 1380.7333 | 1378.4167 | 1377.2583 | 1374.9417 | 1372.625 | 1371.4667 | 1369.15 | 1366.8333 | 1365.675 | 1363.3583 | 1362.2 | 1359.8833 | 1357.5667 | 1356.4083 | 1354.0917 | 1352.9333 | 1350.6167 | 1348.3 | 1347.1417 | 1344.825 | 1343.6667 | 1341.35 | 1339.0333 | 1337.875 | 1335.5583 | 1334.4 | 1332.0833 | 1330.925
| Pumped hydro 24 hrs | Pumped hydro 24 hrs | Vic | Vic | 4 Degrees | 2240.625 | 2236.875 | 2235 | 2231.25 | 2229.375 | 2225.625 | 2221.875 | 2220 | 2216.25 | 2212.5 | 2210.625 | 2206.875 | 2205 | 2201.25 | 2197.5 | 2195.625 | 2191.875 | 2190 | 2186.25 | 2182.5 | 2180.625 | 2176.875 | 2175 | 2171.25 | 2167.5 | 2165.625 | 2161.875 | 2160 | 2156.25 | 2154.375
2 degree scenario
| Technology Type | Generator Name | Region | Regional Cost Zone | Cost Scenario | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Large scale Solar PV | Barcaldine | Qld | Qld medium | 2 Degrees | 1293.2637 | 1242.2977 | 1191.3316 | 1147.7981 | 1046.9278 | 958.799 | 931.1924 | 905.7093 | 881.2881 | 867.4848 | 839.8782 | 829.2602 | 816.5187 | 799.53 | 792.0975 | 772.9852 | 769.7998 | 759.1819 | 753.8729 | 742.1932 | 730.5135 | 724.1427 | 706.0923 | 684.8564 | 671.0531 | 645.5701 | 642.3847 | 629.6432 | 617.9635 | 614.7781
| Large scale Solar PV | Darling Downs | Qld | Qld medium | 2 Degrees | 1293.2637 | 1242.2977 | 1191.3316 | 1147.7981 | 1046.9278 | 958.799 | 931.1924 | 905.7093 | 881.2881 | 867.4848 | 839.8782 | 829.2602 | 816.5187 | 799.53 | 792.0975 | 772.9852 | 769.7998 | 759.1819 | 753.8729 | 742.1932 | 730.5135 | 724.1427 | 706.0923 | 684.8564 | 671.0531 | 645.5701 | 642.3847 | 629.6432 | 617.9635 | 614.7781
| Large scale Solar PV | Fitzroy | Qld | Qld low | 2 Degrees | 1226.3805 | 1178.0503 | 1129.72 | 1088.4379 | 992.7842 | 909.2131 | 883.0343 | 858.8691 | 835.7109 | 822.6214 | 796.4425 | 786.3737 | 774.2911 | 758.1811 | 751.1329 | 733.009 | 729.9884 | 719.9196 | 714.8852 | 703.8095 | 692.7338 | 686.6925 | 669.5756 | 649.438 | 636.3485 | 612.1834 | 609.1627 | 597.0802 | 586.0045 | 582.9838
| Large scale Solar PV | Isaac | Qld | Qld low | 2 Degrees | 1226.3805 | 1178.0503 | 1129.72 | 1088.4379 | 992.7842 | 909.2131 | 883.0343 | 858.8691 | 835.7109 | 822.6214 | 796.4425 | 786.3737 | 774.2911 | 758.1811 | 751.1329 | 733.009 | 729.9884 | 719.9196 | 714.8852 | 703.8095 | 692.7338 | 686.6925 | 669.5756 | 649.438 | 636.3485 | 612.1834 | 609.1627 | 597.0802 | 586.0045 | 582.9838
| Large scale Solar PV | North Queensland Clean Energy Hub | Qld | Qld medium | 2 Degrees | 1293.2637 | 1242.2977 | 1191.3316 | 1147.7981 | 1046.9278 | 958.799 | 931.1924 | 905.7093 | 881.2881 | 867.4848 | 839.8782 | 829.2602 | 816.5187 | 799.53 | 792.0975 | 772.9852 | 769.7998 | 759.1819 | 753.8729 | 742.1932 | 730.5135 | 724.1427 | 706.0923 | 684.8564 | 671.0531 | 645.5701 | 642.3847 | 629.6432 | 617.9635 | 614.7781
| Large scale Solar PV | Northern Queensland | Qld | Qld low | 2 Degrees | 1226.3805 | 1178.0503 | 1129.72 | 1088.4379 | 992.7842 | 909.2131 | 883.0343 | 858.8691 | 835.7109 | 822.6214 | 796.4425 | 786.3737 | 774.2911 | 758.1811 | 751.1329 | 733.009 | 729.9884 | 719.9196 | 714.8852 | 703.8095 | 692.7338 | 686.6925 | 669.5756 | 649.438 | 636.3485 | 612.1834 | 609.1627 | 597.0802 | 586.0045 | 582.9838
| Large scale Solar PV | Broken Hill | NSW | NSW high | 2 Degrees | 1358.5436 | 1305.0049 | 1251.4663 | 1205.7353 | 1099.7734 | 1007.1961 | 978.196 | 951.4267 | 925.7727 | 911.2727 | 882.2726 | 871.1187 | 857.734 | 839.8878 | 832.0801 | 812.0031 | 808.6569 | 797.503 | 791.9261 | 779.6568 | 767.3875 | 760.6952 | 741.7336 | 719.4258 | 704.9257 | 678.1564 | 674.8102 | 661.4256 | 649.1563 | 645.8101
| Large scale Solar PV | Central West New South Wales | NSW | NSW high | 2 Degrees | 1358.5436 | 1305.0049 | 1251.4663 | 1205.7353 | 1099.7734 | 1007.1961 | 978.196 | 951.4267 | 925.7727 | 911.2727 | 882.2726 | 871.1187 | 857.734 | 839.8878 | 832.0801 | 812.0031 | 808.6569 | 797.503 | 791.9261 | 779.6568 | 767.3875 | 760.6952 | 741.7336 | 719.4258 | 704.9257 | 678.1564 | 674.8102 | 661.4256 | 649.1563 | 645.8101
| Large scale Solar PV | Murray River (NSW) | NSW | NSW high | 2 Degrees | 1358.5436 | 1305.0049 | 1251.4663 | 1205.7353 | 1099.7734 | 1007.1961 | 978.196 | 951.4267 | 925.7727 | 911.2727 | 882.2726 | 871.1187 | 857.734 | 839.8878 | 832.0801 | 812.0031 | 808.6569 | 797.503 | 791.9261 | 779.6568 | 767.3875 | 760.6952 | 741.7336 | 719.4258 | 704.9257 | 678.1564 | 674.8102 | 661.4256 | 649.1563 | 645.8101
| Large scale Solar PV | North West New South Wales | NSW | NSW medium | 2 Degrees | 1295.6688 | 1244.6079 | 1193.5471 | 1149.9326 | 1048.8747 | 960.582 | 932.9241 | 907.3937 | 882.927 | 869.098 | 841.4401 | 830.8024 | 818.0372 | 801.0169 | 793.5705 | 774.4227 | 771.2314 | 760.5937 | 755.2749 | 743.5735 | 731.872 | 725.4894 | 707.4054 | 686.13 | 672.301 | 646.7706 | 643.5793 | 630.8141 | 619.1127 | 615.9214
| Large scale Solar PV | New England | NSW | NSW low | 2 Degrees | 1232.794 | 1184.211 | 1135.628 | 1094.13 | 997.9761 | 913.968 | 887.6522 | 863.3606 | 840.0813 | 826.9234 | 800.6076 | 790.4861 | 778.3404 | 762.146 | 755.061 | 736.8424 | 733.8059 | 723.6845 | 718.6237 | 707.4901 | 696.3565 | 690.2837 | 673.0772 | 652.8343 | 639.6764 | 615.3848 | 612.3484 | 600.2027 | 589.069 | 586.0326
| Large scale Solar PV | Riverland (NSW) | NSW | NSW high | 2 Degrees | 1358.5436 | 1305.0049 | 1251.4663 | 1205.7353 | 1099.7734 | 1007.1961 | 978.196 | 951.4267 | 925.7727 | 911.2727 | 882.2726 | 871.1187 | 857.734 | 839.8878 | 832.0801 | 812.0031 | 808.6569 | 797.503 | 791.9261 | 779.6568 | 767.3875 | 760.6952 | 741.7336 | 719.4258 | 704.9257 | 678.1564 | 674.8102 | 661.4256 | 649.1563 | 645.8101
| Large scale Solar PV | Southern New South Wales Tablelands | NSW | NSW low | 2 Degrees | 1232.794 | 1184.211 | 1135.628 | 1094.13 | 997.9761 | 913.968 | 887.6522 | 863.3606 | 840.0813 | 826.9234 | 800.6076 | 790.4861 | 778.3404 | 762.146 | 755.061 | 736.8424 | 733.8059 | 723.6845 | 718.6237 | 707.4901 | 696.3565 | 690.2837 | 673.0772 | 652.8343 | 639.6764 | 615.3848 | 612.3484 | 600.2027 | 589.069 | 586.0326
| Large scale Solar PV | Murray River | NSW | NSW high | 2 Degrees | 1358.5436 | 1305.0049 | 1251.4663 | 1205.7353 | 1099.7734 | 1007.1961 | 978.196 | 951.4267 | 925.7727 | 911.2727 | 882.2726 | 871.1187 | 857.734 | 839.8878 | 832.0801 | 812.0031 | 808.6569 | 797.503 | 791.9261 | 779.6568 | 767.3875 | 760.6952 | 741.7336 | 719.4258 | 704.9257 | 678.1564 | 674.8102 | 661.4256 | 649.1563 | 645.8101
| Large scale Solar PV | Eastern Eyre Peninsula | SA | SA medium | 2 Degrees | 1285.2469 | 1234.5968 | 1183.9467 | 1140.683 | 1040.438 | 952.8555 | 925.42 | 900.0949 | 875.8251 | 862.1073 | 834.6718 | 824.1197 | 811.4572 | 794.5738 | 787.1874 | 768.1936 | 765.0279 | 754.4758 | 749.1998 | 737.5924 | 725.9851 | 719.6539 | 701.7153 | 680.611 | 666.8933 | 641.5682 | 638.4026 | 625.7401 | 614.1328 | 610.9671
| Large scale Solar PV | Leigh Creek | SA | SA medium | 2 Degrees | 1285.2469 | 1234.5968 | 1183.9467 | 1140.683 | 1040.438 | 952.8555 | 925.42 | 900.0949 | 875.8251 | 862.1073 | 834.6718 | 824.1197 | 811.4572 | 794.5738 | 787.1874 | 768.1936 | 765.0279 | 754.4758 | 749.1998 | 737.5924 | 725.9851 | 719.6539 | 701.7153 | 680.611 | 666.8933 | 641.5682 | 638.4026 | 625.7401 | 614.1328 | 610.9671
| Large scale Solar PV | Northern South Australia | SA | SA medium | 2 Degrees | 1285.2469 | 1234.5968 | 1183.9467 | 1140.683 | 1040.438 | 952.8555 | 925.42 | 900.0949 | 875.8251 | 862.1073 | 834.6718 | 824.1197 | 811.4572 | 794.5738 | 787.1874 | 768.1936 | 765.0279 | 754.4758 | 749.1998 | 737.5924 | 725.9851 | 719.6539 | 701.7153 | 680.611 | 666.8933 | 641.5682 | 638.4026 | 625.7401 | 614.1328 | 610.9671
| Large scale Solar PV | Riverland (SA) | SA | SA medium | 2 Degrees | 1285.2469 | 1234.5968 | 1183.9467 | 1140.683 | 1040.438 | 952.8555 | 925.42 | 900.0949 | 875.8251 | 862.1073 | 834.6718 | 824.1197 | 811.4572 | 794.5738 | 787.1874 | 768.1936 | 765.0279 | 754.4758 | 749.1998 | 737.5924 | 725.9851 | 719.6539 | 701.7153 | 680.611 | 666.8933 | 641.5682 | 638.4026 | 625.7401 | 614.1328 | 610.9671
| Large scale Solar PV | Roxby Downs | SA | SA medium | 2 Degrees | 1285.2469 | 1234.5968 | 1183.9467 | 1140.683 | 1040.438 | 952.8555 | 925.42 | 900.0949 | 875.8251 | 862.1073 | 834.6718 | 824.1197 | 811.4572 | 794.5738 | 787.1874 | 768.1936 | 765.0279 | 754.4758 | 749.1998 | 737.5924 | 725.9851 | 719.6539 | 701.7153 | 680.611 | 666.8933 | 641.5682 | 638.4026 | 625.7401 | 614.1328 | 610.9671
| Large scale Solar PV | Western Eyre Peninsula | SA | SA medium | 2 Degrees | 1285.2469 | 1234.5968 | 1183.9467 | 1140.683 | 1040.438 | 952.8555 | 925.42 | 900.0949 | 875.8251 | 862.1073 | 834.6718 | 824.1197 | 811.4572 | 794.5738 | 787.1874 | 768.1936 | 765.0279 | 754.4758 | 749.1998 | 737.5924 | 725.9851 | 719.6539 | 701.7153 | 680.611 | 666.8933 | 641.5682 | 638.4026 | 625.7401 | 614.1328 | 610.9671
| Wind | Barcaldine | Qld | Qld medium | 2 Degrees | 1996.7183 | 1980.7601 | 1964.945 | 1926.5937 | 1904.2887 | 1878.2722 | 1857.3496 | 1835.6419 | 1824.7326 | 1799.5144 | 1784.0756 | 1767.8178 | 1752.6475 | 1735.7192 | 1719.8747 | 1706.0362 | 1696.0421 | 1684.276 | 1675.3806 | 1663.7987 | 1647.7307 | 1639.0966 | 1630.5336 | 1615.7047 | 1606.4056 | 1597.1821 | 1587.1391 | 1576.2866 | 1566.4082 | 1553.9585
| Wind | Darling Downs | Qld | Qld low | 2 Degrees | 1875.2721 | 1860.2845 | 1845.4313 | 1809.4126 | 1788.4644 | 1764.0302 | 1744.3802 | 1723.9928 | 1713.7471 | 1690.0628 | 1675.5629 | 1660.294 | 1646.0464 | 1630.1477 | 1615.267 | 1602.2702 | 1592.8839 | 1581.8334 | 1573.4791 | 1562.6016 | 1547.5109 | 1539.402 | 1531.3598 | 1517.4328 | 1508.6993 | 1500.0368 | 1490.6047 | 1480.4122 | 1471.1347 | 1459.4422
| Wind | Fitzroy | Qld | Qld low | 2 Degrees | 1875.2721 | 1860.2845 | 1845.4313 | 1809.4126 | 1788.4644 | 1764.0302 | 1744.3802 | 1723.9928 | 1713.7471 | 1690.0628 | 1675.5629 | 1660.294 | 1646.0464 | 1630.1477 | 1615.267 | 1602.2702 | 1592.8839 | 1581.8334 | 1573.4791 | 1562.6016 | 1547.5109 | 1539.402 | 1531.3598 | 1517.4328 | 1508.6993 | 1500.0368 | 1490.6047 | 1480.4122 | 1471.1347 | 1459.4422
| Wind | Isaac | Qld | Qld low | 2 Degrees | 1875.2721 | 1860.2845 | 1845.4313 | 1809.4126 | 1788.4644 | 1764.0302 | 1744.3802 | 1723.9928 | 1713.7471 | 1690.0628 | 1675.5629 | 1660.294 | 1646.0464 | 1630.1477 | 1615.267 | 1602.2702 | 1592.8839 | 1581.8334 | 1573.4791 | 1562.6016 | 1547.5109 | 1539.402 | 1531.3598 | 1517.4328 | 1508.6993 | 1500.0368 | 1490.6047 | 1480.4122 | 1471.1347 | 1459.4422
| Wind | North Queensland Clean Energy Hub | Qld | Qld medium | 2 Degrees | 1996.7183 | 1980.7601 | 1964.945 | 1926.5937 | 1904.2887 | 1878.2722 | 1857.3496 | 1835.6419 | 1824.7326 | 1799.5144 | 1784.0756 | 1767.8178 | 1752.6475 | 1735.7192 | 1719.8747 | 1706.0362 | 1696.0421 | 1684.276 | 1675.3806 | 1663.7987 | 1647.7307 | 1639.0966 | 1630.5336 | 1615.7047 | 1606.4056 | 1597.1821 | 1587.1391 | 1576.2866 | 1566.4082 | 1553.9585
| Wind | Broken Hill | NSW | NSW high | 2 Degrees | 2112.8066 | 2095.9205 | 2079.1859 | 2038.6049 | 2015.0032 | 1987.4741 | 1965.335 | 1942.3652 | 1930.8217 | 1904.1374 | 1887.8009 | 1870.5979 | 1854.5456 | 1836.6331 | 1819.8674 | 1805.2244 | 1794.6492 | 1782.199 | 1772.7865 | 1760.5311 | 1743.529 | 1734.3929 | 1725.3321 | 1709.641 | 1699.8012 | 1690.0415 | 1679.4146 | 1667.9311 | 1657.4784 | 1644.3049
| Wind | Central West New South Wales | NSW | NSW high | 2 Degrees | 2112.8066 | 2095.9205 | 2079.1859 | 2038.6049 | 2015.0032 | 1987.4741 | 1965.335 | 1942.3652 | 1930.8217 | 1904.1374 | 1887.8009 | 1870.5979 | 1854.5456 | 1836.6331 | 1819.8674 | 1805.2244 | 1794.6492 | 1782.199 | 1772.7865 | 1760.5311 | 1743.529 | 1734.3929 | 1725.3321 | 1709.641 | 1699.8012 | 1690.0415 | 1679.4146 | 1667.9311 | 1657.4784 | 1644.3049
| Wind | Murray River (NSW) | Vic | NSW high | 2 Degrees | 1937.7812 | 1922.294 | 1906.9457 | 1869.7264 | 1848.0798 | 1822.8312 | 1802.5262 | 1781.4592 | 1770.872 | 1746.3982 | 1731.415 | 1715.6371 | 1700.9146 | 1684.4859 | 1669.1092 | 1655.6792 | 1645.98 | 1634.5612 | 1625.9284 | 1614.6883 | 1599.0946 | 1590.7154 | 1582.4051 | 1568.0139 | 1558.9893 | 1550.0381 | 1540.2915 | 1529.7593 | 1520.1725 | 1508.0903
| Wind | North West New South Wales | NSW | NSW medium | 2 Degrees | 2004.7552 | 1988.7327 | 1972.8539 | 1934.3483 | 1911.9536 | 1885.8323 | 1864.8255 | 1843.0304 | 1832.0772 | 1806.7576 | 1791.2565 | 1774.9333 | 1759.702 | 1742.7055 | 1726.7973 | 1712.9031 | 1702.8687 | 1691.0553 | 1682.1241 | 1670.4955 | 1654.3629 | 1645.694 | 1637.0966 | 1622.2079 | 1612.8714 | 1603.6108 | 1593.5274 | 1582.6312 | 1572.713 | 1560.2132
| Wind | New England | NSW | NSW low | 2 Degrees | 1896.7038 | 1881.5449 | 1866.522 | 1830.0916 | 1808.904 | 1784.1906 | 1764.316 | 1743.6956 | 1733.3328 | 1709.3778 | 1694.7122 | 1679.2688 | 1664.8583 | 1648.7779 | 1633.7271 | 1620.5818 | 1611.0883 | 1599.9115 | 1591.4617 | 1580.4599 | 1565.1968 | 1556.9952 | 1548.8611 | 1534.7749 | 1525.9416 | 1517.1801 | 1507.6402 | 1497.3312 | 1487.9476 | 1476.1216
| Wind | Riverland (NSW) | NSW | NSW high | 2 Degrees | 2112.8066 | 2095.9205 | 2079.1859 | 2038.6049 | 2015.0032 | 1987.4741 | 1965.335 | 1942.3652 | 1930.8217 | 1904.1374 | 1887.8009 | 1870.5979 | 1854.5456 | 1836.6331 | 1819.8674 | 1805.2244 | 1794.6492 | 1782.199 | 1772.7865 | 1760.5311 | 1743.529 | 1734.3929 | 1725.3321 | 1709.641 | 1699.8012 | 1690.0415 | 1679.4146 | 1667.9311 | 1657.4784 | 1644.3049
| Wind | Southern New South Wales Tablelands | NSW | NSW low | 2 Degrees | 1896.7038 | 1881.5449 | 1866.522 | 1830.0916 | 1808.904 | 1784.1906 | 1764.316 | 1743.6956 | 1733.3328 | 1709.3778 | 1694.7122 | 1679.2688 | 1664.8583 | 1648.7779 | 1633.7271 | 1620.5818 | 1611.0883 | 1599.9115 | 1591.4617 | 1580.4599 | 1565.1968 | 1556.9952 | 1548.8611 | 1534.7749 | 1525.9416 | 1517.1801 | 1507.6402 | 1497.3312 | 1487.9476 | 1476.1216
| Wind | Gippsland | Vic | Vic medium | 2 Degrees | 1902.0617 | 1886.86 | 1871.7946 | 1835.2614 | 1814.0139 | 1789.2307 | 1769.2999 | 1748.6213 | 1738.2292 | 1714.2065 | 1699.4995 | 1684.0125 | 1669.5613 | 1653.4355 | 1638.3422 | 1625.1597 | 1615.6394 | 1604.4311 | 1595.9574 | 1584.9245 | 1569.6182 | 1561.3935 | 1553.2364 | 1539.1104 | 1530.2522 | 1521.4659 | 1511.899 | 1501.561 | 1492.1509 | 1480.2914
| Wind | Moyne | Vic | Vic medium | 2 Degrees | 1902.0617 | 1886.86 | 1871.7946 | 1835.2614 | 1814.0139 | 1789.2307 | 1769.2999 | 1748.6213 | 1738.2292 | 1714.2065 | 1699.4995 | 1684.0125 | 1669.5613 | 1653.4355 | 1638.3422 | 1625.1597 | 1615.6394 | 1604.4311 | 1595.9574 | 1584.9245 | 1569.6182 | 1561.3935 | 1553.2364 | 1539.1104 | 1530.2522 | 1521.4659 | 1511.899 | 1501.561 | 1492.1509 | 1480.2914
| Wind | Murray River | Vic | Vic high | 2 Degrees | 1937.7812 | 1922.294 | 1906.9457 | 1869.7264 | 1848.0798 | 1822.8312 | 1802.5262 | 1781.4592 | 1770.872 | 1746.3982 | 1731.415 | 1715.6371 | 1700.9146 | 1684.4859 | 1669.1092 | 1655.6792 | 1645.98 | 1634.5612 | 1625.9284 | 1614.6883 | 1599.0946 | 1590.7154 | 1582.4051 | 1568.0139 | 1558.9893 | 1550.0381 | 1540.2915 | 1529.7593 | 1520.1725 | 1508.0903
| Wind | Western Victoria | Vic | Vic high | 2 Degrees | 1937.7812 | 1922.294 | 1906.9457 | 1869.7264 | 1848.0798 | 1822.8312 | 1802.5262 | 1781.4592 | 1770.872 | 1746.3982 | 1731.415 | 1715.6371 | 1700.9146 | 1684.4859 | 1669.1092 | 1655.6792 | 1645.98 | 1634.5612 | 1625.9284 | 1614.6883 | 1599.0946 | 1590.7154 | 1582.4051 | 1568.0139 | 1558.9893 | 1550.0381 | 1540.2915 | 1529.7593 | 1520.1725 | 1508.0903
| Wind | Eastern Eyre Peninsula | SA | SA medium | 2 Degrees | 1969.9287 | 1954.1846 | 1938.5817 | 1900.7449 | 1878.7392 | 1853.0718 | 1832.4299 | 1811.0134 | 1800.2505 | 1775.3707 | 1760.1389 | 1744.0993 | 1729.1325 | 1712.4313 | 1696.7995 | 1683.1467 | 1673.2866 | 1661.6784 | 1652.9023 | 1641.4758 | 1625.6234 | 1617.1051 | 1608.657 | 1594.0271 | 1584.8527 | 1575.753 | 1565.8447 | 1555.1378 | 1545.3919 | 1533.1093
| Wind | Leigh Creek | SA | SA medium | 2 Degrees | 1969.9287 | 1954.1846 | 1938.5817 | 1900.7449 | 1878.7392 | 1853.0718 | 1832.4299 | 1811.0134 | 1800.2505 | 1775.3707 | 1760.1389 | 1744.0993 | 1729.1325 | 1712.4313 | 1696.7995 | 1683.1467 | 1673.2866 | 1661.6784 | 1652.9023 | 1641.4758 | 1625.6234 | 1617.1051 | 1608.657 | 1594.0271 | 1584.8527 | 1575.753 | 1565.8447 | 1555.1378 | 1545.3919 | 1533.1093
| Wind | Mid-North South Australia | SA | SA Low | 2 Degrees | 1853.8404 | 1839.0241 | 1824.3407 | 1788.7336 | 1768.0248 | 1743.8699 | 1724.4444 | 1704.29 | 1694.1614 | 1670.7477 | 1656.4136 | 1641.3192 | 1627.2344 | 1611.5174 | 1596.8068 | 1583.9585 | 1574.6795 | 1563.7553 | 1555.4965 | 1544.7433 | 1529.8251 | 1521.8088 | 1513.8586 | 1500.0907 | 1491.457 | 1482.8935 | 1473.5692 | 1463.4932 | 1454.3217 | 1442.7629
| Wind | Northern South Australia | SA | SA medium | 2 Degrees | 1969.9287 | 1954.1846 | 1938.5817 | 1900.7449 | 1878.7392 | 1853.0718 | 1832.4299 | 1811.0134 | 1800.2505 | 1775.3707 | 1760.1389 | 1744.0993 | 1729.1325 | 1712.4313 | 1696.7995 | 1683.1467 | 1673.2866 | 1661.6784 | 1652.9023 | 1641.4758 | 1625.6234 | 1617.1051 | 1608.657 | 1594.0271 | 1584.8527 | 1575.753 | 1565.8447 | 1555.1378 | 1545.3919 | 1533.1093
| Wind | Riverland (SA) | SA | SA Low | 2 Degrees | 1853.8404 | 1839.0241 | 1824.3407 | 1788.7336 | 1768.0248 | 1743.8699 | 1724.4444 | 1704.29 | 1694.1614 | 1670.7477 | 1656.4136 | 1641.3192 | 1627.2344 | 1611.5174 | 1596.8068 | 1583.9585 | 1574.6795 | 1563.7553 | 1555.4965 | 1544.7433 | 1529.8251 | 1521.8088 | 1513.8586 | 1500.0907 | 1491.457 | 1482.8935 | 1473.5692 | 1463.4932 | 1454.3217 | 1442.7629
| Wind | South East South Australia | SA | SA medium | 2 Degrees | 1969.9287 | 1954.1846 | 1938.5817 | 1900.7449 | 1878.7392 | 1853.0718 | 1832.4299 | 1811.0134 | 1800.2505 | 1775.3707 | 1760.1389 | 1744.0993 | 1729.1325 | 1712.4313 | 1696.7995 | 1683.1467 | 1673.2866 | 1661.6784 | 1652.9023 | 1641.4758 | 1625.6234 | 1617.1051 | 1608.657 | 1594.0271 | 1584.8527 | 1575.753 | 1565.8447 | 1555.1378 | 1545.3919 | 1533.1093
| Wind | Western Eyre Peninsula | SA | SA medium | 2 Degrees | 1969.9287 | 1954.1846 | 1938.5817 | 1900.7449 | 1878.7392 | 1853.0718 | 1832.4299 | 1811.0134 | 1800.2505 | 1775.3707 | 1760.1389 | 1744.0993 | 1729.1325 | 1712.4313 | 1696.7995 | 1683.1467 | 1673.2866 | 1661.6784 | 1652.9023 | 1641.4758 | 1625.6234 | 1617.1051 | 1608.657 | 1594.0271 | 1584.8527 | 1575.753 | 1565.8447 | 1555.1378 | 1545.3919 | 1533.1093
| Wind | Yorke Peninsula | SA | SA Low | 2 Degrees | 1853.8404 | 1839.0241 | 1824.3407 | 1788.7336 | 1768.0248 | 1743.8699 | 1724.4444 | 1704.29 | 1694.1614 | 1670.7477 | 1656.4136 | 1641.3192 | 1627.2344 | 1611.5174 | 1596.8068 | 1583.9585 | 1574.6795 | 1563.7553 | 1555.4965 | 1544.7433 | 1529.8251 | 1521.8088 | 1513.8586 | 1500.0907 | 1491.457 | 1482.8935 | 1473.5692 | 1463.4932 | 1454.3217 | 1442.7629
| Wind | North East Tasmania | Tas | Tas high | 2 Degrees | 2077.9801 | 2061.3724 | 2044.9136 | 2005.0015 | 1981.7888 | 1954.7135 | 1932.9394 | 1910.3482 | 1898.995 | 1872.7505 | 1856.6833 | 1839.7639 | 1823.9762 | 1806.3589 | 1789.8696 | 1775.4679 | 1765.0671 | 1752.8221 | 1743.5647 | 1731.5114 | 1714.7895 | 1705.804 | 1696.8925 | 1681.4601 | 1671.7825 | 1662.1837 | 1651.732 | 1640.4377 | 1630.1573 | 1617.201
| Wind | North West Tasmania | Tas | Tas medium | 2 Degrees | 1972.6076 | 1956.8421 | 1941.218 | 1903.3298 | 1881.2942 | 1855.5918 | 1834.9219 | 1813.4762 | 1802.6987 | 1777.7851 | 1762.5326 | 1746.4712 | 1731.484 | 1714.7601 | 1699.107 | 1685.4356 | 1675.5622 | 1663.9381 | 1655.1502 | 1643.7081 | 1627.8341 | 1619.3043 | 1610.8447 | 1596.1948 | 1587.008 | 1577.8959 | 1567.9742 | 1557.2527 | 1547.4936 | 1535.1942
| Wind | Tasmania Midlands | Tas | Tas medium | 2 Degrees | 1972.6076 | 1956.8421 | 1941.218 | 1903.3298 | 1881.2942 | 1855.5918 | 1834.9219 | 1813.4762 | 1802.6987 | 1777.7851 | 1762.5326 | 1746.4712 | 1731.484 | 1714.7601 | 1699.107 | 1685.4356 | 1675.5622 | 1663.9381 | 1655.1502 | 1643.7081 | 1627.8341 | 1619.3043 | 1610.8447 | 1596.1948 | 1587.008 | 1577.8959 | 1567.9742 | 1557.2527 | 1547.4936 | 1535.1942
| OCGT | OCGT | QLD | Qld low | 2 Degrees | 895.7191 | 894.7127 | 892.6998 | 891.6934 | 889.6805 | 888.6741 | 886.6613 | 885.6548 | 884.6484 | 882.6356 | 881.6291 | 879.6163 | 878.6099 | 877.6034 | 875.5906 | 874.5842 | 872.5713 | 871.5649 | 870.5585 | 868.5456 | 867.5392 | 866.5328 | 864.5199 | 863.5135 | 861.5006 | 860.4942 | 859.4878 | 857.4749 | 856.4685 | 855.4621
| OCGT | OCGT | NSW | NSW low | 2 Degrees | 899.9709 | 898.9597 | 896.9373 | 895.9261 | 893.9037 | 892.8925 | 890.8701 | 889.8589 | 888.8477 | 886.8252 | 885.814 | 883.7916 | 882.7804 | 881.7692 | 879.7468 | 878.7356 | 876.7132 | 875.702 | 874.6908 | 872.6684 | 871.6572 | 870.646 | 868.6236 | 867.6124 | 865.59 | 864.5788 | 863.5676 | 861.5452 | 860.534 | 859.5228
| OCGT | OCGT | SA | SA low | 2 Degrees | 891.4673 | 890.4657 | 888.4624 | 887.4607 | 885.4574 | 884.4558 | 882.4525 | 881.4508 | 880.4492 | 878.4459 | 877.4442 | 875.4409 | 874.4393 | 873.4376 | 871.4343 | 870.4327 | 868.4294 | 867.4278 | 866.4261 | 864.4228 | 863.4212 | 862.4195 | 860.4162 | 859.4146 | 857.4113 | 856.4096 | 855.408 | 853.4047 | 852.403 | 851.4014
| OCGT | OCGT | Tas | Tas low | 2 Degrees | 894.1253 | 893.1207 | 891.1114 | 890.1068 | 888.0975 | 887.0929 | 885.0836 | 884.079 | 883.0743 | 881.0651 | 880.0604 | 878.0512 | 877.0465 | 876.0419 | 874.0326 | 873.028 | 871.0187 | 870.0141 | 869.0094 | 867.0002 | 865.9955 | 864.9909 | 862.9816 | 861.977 | 859.9677 | 858.9631 | 857.9585 | 855.9492 | 854.9445 | 853.9399
| OCGT | OCGT | Vic | Vic low | 2 Degrees | 890.4044 | 889.4039 | 887.403 | 886.4026 | 884.4016 | 883.4012 | 881.4003 | 880.3998 | 879.3994 | 877.3985 | 876.398 | 874.3971 | 873.3967 | 872.3962 | 870.3953 | 869.3948 | 867.3939 | 866.3935 | 865.393 | 863.3921 | 862.3917 | 861.3912 | 859.3903 | 858.3898 | 856.3889 | 855.3885 | 854.388 | 852.3871 | 851.3867 | 850.3862
| CCGT | CCGT | QLD | Qld low | 2 Degrees | 1280.5669 | 1278.5534 | 1276.54 | 1274.5265 | 1272.513 | 1270.4996 | 1268.4861 | 1266.4726 | 1264.4592 | 1262.4457 | 1260.4322 | 1258.4187 | 1256.4053 | 1254.3918 | 1252.3783 | 1250.3649 | 1248.3514 | 1246.3379 | 1244.3245 | 1242.311 | 1240.2975 | 1238.284 | 1236.2706 | 1234.2571 | 1232.2436 | 1230.2302 | 1228.2167 | 1226.2032 | 1224.1898 | 1222.1763
| CCGT | CCGT | NSW | NSW low | 2 Degrees | 1287.3575 | 1285.3334 | 1283.3092 | 1281.2851 | 1279.261 | 1277.2368 | 1275.2127 | 1273.1885 | 1271.1644 | 1269.1402 | 1267.1161 | 1265.0919 | 1263.0678 | 1261.0436 | 1259.0195 | 1256.9953 | 1254.9712 | 1252.947 | 1250.9229 | 1248.8987 | 1246.8746 | 1244.8505 | 1242.8263 | 1240.8022 | 1238.778 | 1236.7539 | 1234.7297 | 1232.7056 | 1230.6814 | 1228.6573
| CCGT | CCGT | SA | SA low | 2 Degrees | 1273.7763 | 1271.7735 | 1269.7707 | 1267.7679 | 1265.7651 | 1263.7623 | 1261.7595 | 1259.7567 | 1257.7539 | 1255.7511 | 1253.7484 | 1251.7456 | 1249.7428 | 1247.74 | 1245.7372 | 1243.7344 | 1241.7316 | 1239.7288 | 1237.726 | 1235.7232 | 1233.7204 | 1231.7176 | 1229.7148 | 1227.712 | 1225.7093 | 1223.7065 | 1221.7037 | 1219.7009 | 1217.6981 | 1215.6953
| CCGT | CCGT | Tas | Tas low | 2 Degrees | 1278.0211 | 1276.0116 | 1274.0022 | 1271.9927 | 1269.9832 | 1267.9738 | 1265.9643 | 1263.9548 | 1261.9454 | 1259.9359 | 1257.9264 | 1255.917 | 1253.9075 | 1251.898 | 1249.8886 | 1247.8791 | 1245.8696 | 1243.8602 | 1241.8507 | 1239.8412 | 1237.8318 | 1235.8223 | 1233.8128 | 1231.8034 | 1229.7939 | 1227.7844 | 1225.775 | 1223.7655 | 1221.756 | 1219.7466
| CCGT | CCGT | Vic | Vic low | 2 Degrees | 1272.0786 | 1270.0785 | 1268.0784 | 1266.0783 | 1264.0781 | 1262.078 | 1260.0779 | 1258.0778 | 1256.0776 | 1254.0775 | 1252.0774 | 1250.0773 | 1248.0771 | 1246.077 | 1244.0769 | 1242.0768 | 1240.0766 | 1238.0765 | 1236.0764 | 1234.0763 | 1232.0762 | 1230.076 | 1228.0759 | 1226.0758 | 1224.0757 | 1222.0755 | 1220.0754 | 1218.0753 | 1216.0752 | 1214.075
| Battery storage 2hrs | Battery storage 2hrs | QLD | Qld low | 2 Degrees | 1413.1934 | 1366.6397 | 1313.778 | 1253.4408 | 1122.9876 | 1013.6257 | 980.5066 | 967.5842 | 961.5823 | 942.1393 | 941.5813 | 946.1113 | 951.2021 | 954.8506 | 953.5521 | 964.6118 | 972.7796 | 971.644 | 960.6251 | 941.451 | 955.81 | 976.7627 | 979.6704 | 978.1996 | 985.9153 | 972.5744 | 981.3583 | 979.07 | 985.5472 | 985.884
| Battery storage 2hrs | Battery storage 2hrs | NSW | NSW low | 2 Degrees | 1440.8102 | 1393.3468 | 1339.452 | 1277.9358 | 1144.9331 | 1033.4342 | 999.6678 | 986.4929 | 980.3737 | 960.5507 | 959.9818 | 964.6004 | 969.7906 | 973.5105 | 972.1866 | 983.4624 | 991.7898 | 990.632 | 979.3978 | 959.8489 | 974.4886 | 995.8507 | 998.8152 | 997.3157 | 1005.1822 | 991.5806 | 1000.5361 | 998.2031 | 1004.8069 | 1005.1503
| Battery storage 2hrs | Battery storage 2hrs | SA | SA low | 2 Degrees | 1385.5766 | 1339.9326 | 1288.1039 | 1228.9459 | 1101.042 | 993.8173 | 961.3454 | 948.6755 | 942.7909 | 923.7279 | 923.1808 | 927.6223 | 932.6135 | 936.1908 | 934.9176 | 945.7612 | 953.7694 | 952.656 | 941.8524 | 923.053 | 937.1314 | 957.6746 | 960.5255 | 959.0835 | 966.6484 | 953.5682 | 962.1804 | 959.9369 | 966.2875 | 966.6177
| Battery storage 2hrs | Battery storage 2hrs | Tas | Tas low | 2 Degrees | 1402.8371 | 1356.6245 | 1304.1502 | 1244.2552 | 1114.758 | 1006.1976 | 973.3211 | 960.4935 | 954.5355 | 935.235 | 934.6811 | 939.1779 | 944.2314 | 947.8532 | 946.5642 | 957.5428 | 965.6508 | 964.5235 | 953.5854 | 934.5517 | 948.8055 | 969.6047 | 972.491 | 971.031 | 978.6902 | 965.447 | 974.1666 | 971.8951 | 978.3248 | 978.6591
| Battery storage 2hrs | Battery storage 2hrs | Vic | Vic low | 2 Degrees | 1378.6723 | 1333.2558 | 1281.6854 | 1222.8222 | 1095.5556 | 988.8652 | 956.5551 | 943.9484 | 938.093 | 919.125 | 918.5806 | 923 | 927.9664 | 931.5258 | 930.259 | 941.0485 | 949.0169 | 947.909 | 937.1593 | 918.4535 | 932.4618 | 952.9026 | 955.7393 | 954.3044 | 961.8316 | 948.8166 | 957.386 | 955.1536 | 961.4725 | 961.8011

## Refurbishment
TOC
Refurbishment
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Unit refurbishment is staggered within a power station, one unit at a time at six month intervals. In a power station with 4 units, for example, the fourth unit is not refurbished until 18 months after the given date.
Refurbishment timing
| Generator | First refurbishment | Second refurbishment
| Bayswater | 2025
| Eraring | 2024
| Mount Piper | 2023 | 2033
| Vales Point | 2022
| Callide B | 2028
| Callide Power Plant | 2031 | 2041
| Kogan Creek | 2037 | 2047
| Millmerran | 2032 | 2042
| Stanwell | 2026 | 2036
| Tarong | 2026
| Tarong North | 2033 | 2043
| Loy Yang A | 2028 | 2038
| Loy Yang B | 2026 | 2036
| Yallourn | 2022 | 2032

## Retirement
TOC
Retirement
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0 and AEMO 25 June 2019 Project Expected Retirement Date
Announced and end-of-technical-life retirement and according to equipment age. Units may be retired earlier by the model if determined as least cost to the power system.
| End of technical life |  |  |  |  | Retirement Costs
| Generation Name | DUID | AEMO Feb ISP end of life | AEMO 25 June 2019 Project Expected Retirement Date (Calendar year) | Project Marinus assumed retirement date (Calendar year) | Generator | Retirement/Rehabilitation Cost (real 2019 $/MW)
| Angaston | ANGAST1 |  | 2070 | 2070 | Black Coal | 160000
| Appin | APPIN |  | 2036 | 2036 | Brown Coal | 160000
| Bairnsdale | BDL01 |  | 2042 | 2042 | OCGT | 45000
| Bairnsdale | BDL02 |  | 2042 | 2042 | CCGT | 130000
| Bald Hills Wind Farm | BALDHWF1 |  | 2040 | 2040
| Ballarat Energy Storage System | BALBG1 |  | 2033 | 2033 | Changes for end of technical life for Sustained Renewables Uptake scenario
| Ballarat Energy Storage System | BALBL1 |  | 2033 | 2033 | For the Sustained Renewables Uptake scenario, it is assumed that the end of technical life for coal powers stations are
| Banimboola | BAPS |  | 2057 | 2057 | typically brought forward by 3 to 5 years. The table below displays the changes in retirement dates compared to the other
| Bannerton Solar Park | BANN1 |  | 2049 | 2049 | three scenarios, which all have the same fixed retirment schedule as the Status Quo scenario.
| Barcaldine Power Station | BARCALDN |  | 2034 | 2034 | Generation Name | DUID | Status Quo | Sustained Renewables
| Barker Inlet Power Station |  |  | 2044 | 2044 | Bayswater | BW01 | 2035 | 2030
| Barron Gorge | BARRON-1 |  | 2042 | 2042 | Bayswater | BW02 | 2035 | 2030
| Barron Gorge | BARRON-2 |  | 2042 | 2042 | Bayswater | BW03 | 2035 | 2030
| Bastyan | BASTYAN |  | 2100 | 2100 | Bayswater | BW04 | 2035 | 2030
| Bayswater | BW01 | 2035 | 2035 | 2035 | Callide B | CALL_B_1 | 2038 | 2033
| Bayswater | BW02 | 2035 | 2035 | 2035 | Callide B | CALL_B_2 | 2038 | 2033
| Bayswater | BW03 | 2035 | 2035 | 2035 | Callide C | CPP_3 | 2051 | 2046
| Bayswater | BW04 | 2035 | 2035 | 2035 | Callide C | CPP_4 | 2051 | 2046
| Bell Bay Three | BBTHREE1 |  | 2040 | 2040 | Eraring | ER01 | 2031 | 2028
| Bell Bay Three | BBTHREE2 |  | 2040 | 2040 | Eraring | ER02 | 2031 | 2028
| Bell Bay Three | BBTHREE3 |  | 2040 | 2040 | Eraring | ER03 | 2031 | 2028
| Blowering | BLOWERNG |  | 2070 | 2070 | Eraring | ER04 | 2031 | 2028
| Boco Rock Wind Farm | BOCORWF1 |  | 2040 | 2040 | Eraring GT | ERGT01 | 2031 | 2028
| Bogong / Mackay | MCKAY1 |  | 2057 | 2057 | Gladstone | GSTONE1 | 2029 | 2026
| Braemar | BRAEMAR1 |  | 2046 | 2046 | Gladstone | GSTONE2 | 2029 | 2026
| Braemar | BRAEMAR2 |  | 2046 | 2046 | Gladstone | GSTONE3 | 2029 | 2026
| Braemar | BRAEMAR3 |  | 2046 | 2046 | Gladstone | GSTONE4 | 2029 | 2026
| Braemar 2 Power Station | BRAEMAR5 |  | 2049 | 2049 | Gladstone | GSTONE5 | 2029 | 2026
| Braemar 2 Power Station | BRAEMAR6 |  | 2049 | 2049 | Gladstone | GSTONE6 | 2029 | 2026
| Braemar 2 Power Station | BRAEMAR7 |  | 2049 | 2049 | Loy Yang A Power Station | LYA1 | 2048 | 2043
| Broken Hill GT | GB01 |  | 2026 | 2026 | Loy Yang A Power Station | LYA2 | 2048 | 2043
| Broken Hill Solar Plant | BROKENH1 |  | 2043 | 2043 | Loy Yang A Power Station | LYA3 | 2048 | 2043
| Burrendong | BDONGHYD |  | 2036 | 2036 | Loy Yang A Power Station | LYA4 | 2048 | 2043
| Butlers Gorge | BUTLERSG |  | 2100 | 2100 | Loy Yang B | LOYYB1 | 2047 | 2042
| Callide B | CALL_B_1 | 2038 | Not yet submitted | 2038 | Loy Yang B | LOYYB2 | 2047 | 2042
| Callide B | CALL_B_2 | 2038 | Not yet submitted | 2038 | Millmerran | MPP_1 | 2051 | 2046
| Callide C | CPP_3 | 2051 | Not yet submitted | 2051 | Millmerran | MPP_2 | 2051 | 2046
| Callide C | CPP_4 | 2051 | Not yet submitted | 2051 | Mt Piper | MP1 | 2042 | 2037
| Canunda Wind Farm | CNUNDAWF |  | 2030 | 2030 | Mt Piper | MP2 | 2042 | 2037
| Capital East Solar Farm P1 | CESF1 |  | 2043 | 2043 | Stanwell | STAN-1 | 2043 | 2038
| Capital Wind Farm | CAPTL_WF |  | 2040 | 2040 | Stanwell | STAN-2 | 2044 | 2038
| Catagunya / Liapootah / Wayatinah | LI_WY_CA |  | 2100 | 2100 | Stanwell | STAN-3 | 2045 | 2038
| Cethana | CETHANA |  | 2100 | 2100 | Stanwell | STAN-4 | 2046 | 2038
| Clare Solar Farm | CLARESF1 |  | 2047 | 2047 | Tarong | TARONG#1 | 2036 | 2031
| Clayton | CLAYTON |  | 2025 | 2025 | Tarong | TARONG#2 | 2036 | 2031
| Clements Gap Wind Farm | CLEMGPWF |  | 2039 | 2039 | Tarong | TARONG#3 | 2037 | 2032
| Clover | CLOVER |  | 2057 | 2057 | Tarong | TARONG#4 | 2037 | 2032
| Cluny | CLUNY |  | 2100 | 2100 | Tarong North | TNPS1 | 2037 | 2032
| Coleambally Solar Farm | COLEASF1 |  | 2038 | 2038 | Vales Point B | VP5 | 2029 | 2026
| Collinsville PV | CSPVPS1 |  | 2044 | 2044 | Vales Point B | VP6 | 2029 | 2026
| Colongra | CG1 |  | 2070 | 2070 | Yallourn W | YWPS1 | 2029 | 2026
| Colongra | CG2 |  | 2070 | 2070 | Yallourn W | YWPS2 | 2030 | 2027
| Colongra | CG3 |  | 2070 | 2070 | Yallourn W | YWPS3 | 2031 | 2028
| Colongra | CG4 |  | 2070 | 2070 | Yallourn W | YWPS4 | 2032 | 2028
| Condamine A | CPSA |  | 2039 | 2039
| Corio | CORIO1 |  | 2029 | 2029
| Crookwell 2 Wind Farm | CROOKWF2 |  | 2043 | 2043
| Cullerin Range Wind Farm | CULLRGWF |  | 2038 | 2038
| Dalrymple North BESS | DALNTH01 |  | 2030 | 2030
| Darling Downs | DDPS1 |  | 2045 | 2045
| Darling Downs Solar Farm | DDSF1 |  | 2035 | 2035
| Dartmouth | DARTM1 |  | 2057 | 2057
| Daydream Solar Farm | DAYDSF1 |  | 2048 | 2048
| Devils Gate | DEVILS_G |  | 2100 | 2100
| Dry Creek GT | DRYCGT1 |  | 2030 | 2030
| Dry Creek GT | DRYCGT2 |  | 2030 | 2030
| Dry Creek GT | DRYCGT3 |  | 2030 | 2030
| Eastern Creek | EASTCRK |  | 2025 | 2025
| Eildon | EILDON1 |  | 2057 | 2057
| Eildon | EILDON2 |  | 2057 | 2057
| Elaine Wind Farm |  |  | 2049 | 2049
| Eraring | ER01 | 2034 | 2031 | 2031
| Eraring | ER02 | 2034 | 2031 | 2031
| Eraring | ER03 | 2034 | 2031 | 2031
| Eraring | ER04 | 2034 | 2031 | 2031
| Eraring GT | ERGT01 |  | 2031 | 2031
| Fisher | FISHER |  | 2100 | 2100
| Gannawarra Energy Storage System | GANNBG1 |  | 2033 | 2033
| Gannawarra Energy Storage System | GANNBL1 |  | 2034 | 2034
| Gannawarra Solar Farm | GANNSF1 |  | 2048 | 2048
| German Creek | GERMCRK |  | 2036 | 2036
| Gladstone | GSTONE1 | 2029 | Not yet submitted | 2029
| Gladstone | GSTONE2 | 2029 | Not yet submitted | 2029
| Gladstone | GSTONE3 | 2029 | Not yet submitted | 2029
| Gladstone | GSTONE4 | 2029 | Not yet submitted | 2029
| Gladstone | GSTONE5 | 2029 | Not yet submitted | 2029
| Gladstone | GSTONE6 | 2029 | Not yet submitted | 2029
| Gordon | GORDON |  | 2100 | 2100
| Grange Avenue | GRANGEAV |  | 2025 | 2025
| Griffith Solar Farm | GRIFSF1 |  | 2058 | 2058
| Gullen Range Solar Farm | GULLRSF1 |  | 2100 | 2100
| Gullen Range Wind Farm | GULLRWF1 |  | 2100 | 2100
| Gunning Wind Farm | GUNNING1 |  | 2036 | 2036
| Guthega | GUTHEGA |  | 2070 | 2070
| Hallett 4 North Brown Hill | NBHWF1 |  | 2036 | 2036
| Hallett 5 The Bluff WF | BLUFF1 |  | 2036 | 2036
| Hallett Power Station | AGLHAL |  | 2032 | 2032
| Hallett Power Station | AGLHAL |  | 2050 | 2050
| Hallett Power Station | AGLHAL |  | 2032 | 2032
| Hallett Power Station | AGLHAL |  | 2032 | 2032
| Hallett Power Station | AGLHAL |  | 2032 | 2032
| Hallett Power Station | AGLHAL |  | 2032 | 2032
| Hallett Power Station | AGLHAL |  | 2032 | 2032
| Hallett Power Station | AGLHAL |  | 2032 | 2032
| Hallett Power Station | AGLHAL |  | 2032 | 2032
| Hallett Power Station | AGLHAL |  | 2032 | 2032
| Hallett Power Station | AGLHAL |  | 2032 | 2032
| Hallett Power Station | AGLHAL |  | 2032 | 2032
| Hallett Power Station | AGLHAL |  | 2032 | 2032
| Hallett Stage 1 Brown Hill | HALLWF1 |  | 2033 | 2033
| Hallett Stage 2 Hallett Hill | HALLWF2 |  | 2035 | 2035
| Hamilton Solar Farm | HAMISF1 |  | 2048 | 2048
| Hornsdale Power Reserve Unit 1 | HPRG1 |  | 2057 | 2057
| Hornsdale Wind Farm Stage 1 v1 | HDWF1 |  | 2056 | 2056
| Hornsdale Wind Farm Stage 2 | HDWF2 |  | 2057 | 2057
| Hornsdale Wind Farm Stage 3 | HDWF3 |  | 2057 | 2057
| Hume Dam NSW | HUMENSW |  | 2057 | 2057
| Hume Dam VIC | HUMEV |  | 2057 | 2057
| Hunter Valley GT | HVGTS |  | 2035 | 2035
| Jacks Gully | JACKSGUL |  | 2026 | 2026
| Jeeralang A | JLA01 |  | 2039 | 2039
| Jeeralang A | JLA02 |  | 2039 | 2039
| Jeeralang A | JLA03 |  | 2039 | 2039
| Jeeralang A | JLA04 |  | 2039 | 2039
| Jeeralang B | JLB01 |  | 2039 | 2039
| Jeeralang B | JLB02 |  | 2039 | 2039
| Jeeralang B | JLB03 |  | 2039 | 2039
| Jindabyne | JNDABNE1 |  | 2070 | 2070
| John Butters | JBUTTERS |  | 2100 | 2100
| Jounama | JOUNAMA1 |  | 2070 | 2070
| Karadoc Solar Farm | KARSF1 |  | 2048 | 2048
| Kareeya | KAREEYA1 |  | 2037 | 2037
| Kareeya | KAREEYA2 |  | 2037 | 2037
| Kareeya | KAREEYA3 |  | 2037 | 2037
| Kareeya | KAREEYA4 |  | 2037 | 2037
| Kiata Wind Farm | KIATAWF1 |  | 2042 | 2042
| Kidston Solar Project Phase One 50MW | KSP1 |  | 2048 | 2048
| Kogan Creek | KPP_1 | 2057 | Not yet submitted | 2057
| Ladbroke Grove | LADBROK1 |  | 2034 | 2034
| Ladbroke Grove | LADBROK2 |  | 2034 | 2034
| Lake Bonney 1 Wind Farm | LKBONNY1 |  | 2035 | 2035
| Lake Bonney 2 Wind Farm | LKBONNY2 |  | 2038 | 2038
| Lake Bonney 3 Wind Farm | LKBONNY3 |  | 2040 | 2040
| Lake Echo | LK_ECHO |  | 2100 | 2100
| Laverton North | LNGS1 |  | 2070 | 2070
| Laverton North | LNGS2 |  | 2070 | 2070
| Lemonthyme / Wilmot | LEM_WIL |  | 2100 | 2100
| Liddell | LD01 |  | 2022 | 2022
| Liddell | LD02 |  | 2022 | 2022
| Liddell | LD03 |  | 2022 | 2022
| Liddell | LD04 |  | 2022 | 2022
| Lincoln Gap Wind Farm - stage 1 | LGAPWF1 |  | 2045 | 2045
| Lonsdale | LONSDALE |  | 2070 | 2070
| Loy Yang A Power Station | LYA1 |  | 2048 | 2048
| Loy Yang A Power Station | LYA2 |  | 2048 | 2048
| Loy Yang A Power Station | LYA3 |  | 2048 | 2048
| Loy Yang A Power Station | LYA4 |  | 2048 | 2048
| Loy Yang B | LOYYB1 | 2056 | 2047 | 2047
| Loy Yang B | LOYYB2 | 2056 | 2047 | 2047
| Lucas Heights 2 | LUCAS2S2 |  | 2025 | 2025
| Macarthur Wind Farm | MACARTH1 |  | 2038 | 2038
| Mackay GT | MACKAYGT |  | 2021 | 2021
| Mackintosh | MACKNTSH |  | 2100 | 2100
| Meadowbank | MEADOWBK |  | 2100 | 2100
| Millmerran | MPP_1 | 2052 | 2051 | 2051
| Millmerran | MPP_2 | 2052 | 2051 | 2051
| Mintaro GT | MINTARO |  | 2030 | 2030
| Moranbah North | MBAHNTH |  | 2038 | 2038
| Moree Solar Farm | MOREESF1 |  | 2046 | 2046
| Mortlake | MORTLK11 |  | 2046 | 2046
| Mortlake | MORTLK12 |  | 2046 | 2046
| Mount Emerald | MEWF1 |  | 2043 | 2043
| Mt Mercer | MERCER01 |  | 2043 | 2043
| Mt Piper | MP1 | 2043 | 2042 | 2042
| Mt Piper | MP2 | 2043 | 2042 | 2042
| Mt Stuart | MSTUART1 |  | 2033 | 2033
| Mt Stuart | MSTUART2 |  | 2033 | 2033
| Mt Stuart | MSTUART3 |  | 2044 | 2044
| Murray 1 | MURRAY |  | 2070 | 2070
| Murray 2 | MURRAY |  | 2070 | 2070
| Musselroe Wind Farm | MUSSELR1 |  | 2050 | 2050
| Narromine Solar Farm | NASF1 |  | 2058 | 2058
| Newport | NPS | 2031 | 2039 | 2039
| Nyngan Solar Plant | NYNGAN1 |  | 2042 | 2042
| Oakey 1 Solar Farm | OAKEY1SF |  | 2043 | 2043
| Oakey 2 Solar Farm | OAKEY2SF |  | 2044 | 2044
| Oakey Power Station | OAKEY1 |  | 2050 | 2050
| Oakey Power Station | OAKEY2 |  | 2050 | 2050
| Oaklands Hill Wind Farm | OAKLAND1 |  | 2037 | 2037
| Oaky Creek | OAKYCREK |  | 2025 | 2025
| Oaky Creek 2 | OAKY2 |  | 2025 | 2025
| Osborne | OSB-AG |  | 2023 | 2023
| Paloona | PALOONA |  | 2100 | 2100
| Parkes Solar Farm | PARSF1 |  | 2058 | 2058
| Pelican Point | PPCCGT |  | 2037 | 2037
| Poatina | POAT110 |  | 2100 | 2100
| Poatina | POAT220 |  | 2100 | 2100
| Port Lincoln GT | POR01 |  | 2030 | 2030
| Port Lincoln GT | POR03 |  | 2030 | 2030
| Port Stanvac 1 | PTSTAN1 |  | 2070 | 2070
| Quarantine | QPS1 |  | 2052 | 2052
| Quarantine | QPS2 |  | 2053 | 2053
| Quarantine | QPS3 |  | 2053 | 2053
| Quarantine | QPS4 |  | 2054 | 2054
| Quarantine | QPS5 |  | 2044 | 2044
| Reece | REECE1 |  | 2100 | 2100
| Reece | REECE2 |  | 2100 | 2100
| Repulse | REPULSE |  | 2100 | 2100
| Roma | ROMA_7 |  | 2034 | 2034
| Roma | ROMA_8 |  | 2034 | 2034
| Rowallan | ROWALLAN |  | 2100 | 2100
| Royalla Solar Farm | ROYALLA1 |  | 2045 | 2045
| Salt Creek Wind Farm | SALTCRK1 |  | 2043 | 2043
| Sapphire Wind Farm | SAPHWF1 |  | 2037 | 2037
| Shoalhaven | SHGEN |  | 2100 | 2100
| Silverton Wind Farm | STWF1 |  | 2043 | 2043
| Smithfield Energy Facility | SITHE01 |  | 2044 | 2044
| Snowtown S2 Wind Farm | SNOWNTH1 |  | 2034 | 2034
| Snowtown S2 Wind Farm | SNOWSTH1 |  | 2034 | 2034
| Snowtown Wind Farm | SNOWTWN1 |  | 2028 | 2028
| Snuggery | SNUG1 |  | 2030 | 2030
| Somerton | AGLSOM |  | 2033 | 2033
| South Keswick Solar Farm | SKSF1 |  | 2058 | 2058
| Stanwell | STAN-1 | 2046 | 2043 | 2043
| Stanwell | STAN-2 | 2046 | 2044 | 2044
| Stanwell | STAN-3 | 2046 | 2045 | 2045
| Stanwell | STAN-4 | 2046 | 2046 | 2046
| Swanbank E GT | SWAN_E |  | 2028 | 2028
| Tahmoor | TAHMOOR1 |  | 2035 | 2035
| Tallawarra | TALWA1 |  | 2043 | 2043
| Tamar Valley Combined Cycle | TVCC201 |  | 2050 | 2050
| Tamar Valley Peaking | TVPP104 |  | 2050 | 2050
| Taralga Wind Farm | TARALGA1 |  | 2040 | 2040
| Tarong | TARONG#1 | 2036 | 2036 | 2036
| Tarong | TARONG#2 | 2036 | 2036 | 2036
| Tarong | TARONG#3 | 2036 | 2037 | 2037
| Tarong | TARONG#4 | 2036 | 2037 | 2037
| Tarong North | TNPS1 | 2053 | 2037 | 2037
| Tarraleah | TARRALEA |  | 2100 | 2100
| Teralba | TERALBA |  | 2022 | 2022
| Toora | TOORAWF |  | 2032 | 2032
| Torrens Island A | TORRA1 | 2021 | 2035 | 20241
| Torrens Island A | TORRA2 | 2021 | 2035 | 20241
| Torrens Island A | TORRA3 | 2021 | 2035 | 20241
| Torrens Island A | TORRA4 | 2021 | 2035 | 20241
| Torrens Island B | TORRB1 |  | 2035 | 20241
| Torrens Island B | TORRB2 |  | 2035 | 20241
| Torrens Island B | TORRB3 |  | 2035 | 20241
| Torrens Island B | TORRB4 |  | 2035 | 20241
| Tower | TOWER |  | 2036 | 2036
| Townsville Power Station | YABULU |  | 2046 | 2046
| Townsville Power Station | YABULU2 |  | 2046 | 2046
| Trevallyn | TREVALLN |  | 2100 | 2100
| Tribute | TRIBUTE |  | 2100 | 2100
| Tumut 3 | TUMUT3 |  | 2070 | 2070
| Tungatinah | TUNGATIN |  | 2100 | 2100
| Upper Tumut | UPPTUMUT |  | 2070 | 2070
| Uranquinty | URANQ11 |  | 2044 | 2044
| Uranquinty | URANQ12 |  | 2044 | 2044
| Uranquinty | URANQ13 |  | 2044 | 2044
| Uranquinty | URANQ14 |  | 2044 | 2044
| Vales Point B | VP5 | 2028 | 2029 | 2029
| Vales Point B | VP6 | 2028 | 2029 | 2029
| Valley Power | VPGS1 |  | 2070 | 2070
| Valley Power | VPGS2 |  | 2070 | 2070
| Valley Power | VPGS3 |  | 2070 | 2070
| Valley Power | VPGS4 |  | 2070 | 2070
| Valley Power | VPGS5 |  | 2070 | 2070
| Valley Power | VPGS6 |  | 2070 | 2070
| Waterloo Wind Farm | WATERLWF |  | 2045 | 2045
| Waterloo Wind Farm | WATERLWF |  | 2051 | 2051
| Wattle Point | WPWF |  | 2029 | 2029
| West Kiewa | WKIEWA1 |  | 2057 | 2057
| West Kiewa | WKIEWA2 |  | 2057 | 2057
| White Rock Solar Farm | WRSF1 |  | 2043 | 2043
| White Rock Wind Farm - Stage 1 | WRWF1 |  | 2037 | 2037
| Whitsunday Solar Farm | WHITSF1 |  | 2048 | 2048
| Willogoleche Wind Farm | WGWF1 |  | 2043 | 2043
| Windy Hill | WHILL1 |  | 2025 | 2025
| Wivenhoe | W/HOE#1 |  | Not yet submitted
| Wivenhoe | W/HOE#1 |  | Not yet submitted
| Woodlawn Wind Farm | WOODLWN1 |  | 2041 | 2041
| Woolnorth Studland Bay / Bluff Point | WOOLNTH1 |  | 2050 | 2050
| Yallourn W | YWPS1 | 2032 | 2029 | 2029
| Yallourn W | YWPS2 | 2032 | 2030 | 2030
| Yallourn W | YWPS3 | 2032 | 2031 | 2031
| Yallourn W | YWPS4 | 2032 | 2032 | 2032
| Yendon Wind Farm | YENDWF1 |  | 2049 | 2049
1Torrens Island A and Torrens Island B are assumed to retire when Project EnergyConnect becomes operational

## Coal capacity
TOC
Coal capacity constraint for Global Slowdown scenario
Primary source: Aurora Energy Research analysis of AEMO’s ISP Part 2: economics of coal closures
The following NEM coal capacity restriction is in line with the lower NEM-wide demand scenario from Aurora Energy Research’s revenue adequacy report to AEMO. This is applied for the Global Slowdown scenario.
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
| Maximum coal capacity (MW) | 23040 | 23040 | 21240 | 20640 | 20640 | 19180 | 19180 | 19180 | 17860 | 14380 | 13900 | 13900 | 12380 | 10980 | 8780 | 5340 | 4900 | 4900 | 4900 | 4900

## Gas and Liquid fuel price
TOC
Gas prices ($/GJ) real June 2019 dollars
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Prices are the sum of wholesale price and transportation cost.
Based on December 2018 "Delivered Wholesale Gas price Outlook 2019-2040" by Core Energy & Resources Pty Limited
| Fast Change: | To be used in Accelerated Transition to a Low Emissions Future scenario
| Neutral: | To be used in Status Quo scenario and Sustained Renewables Uptake scenario
| Slow Change: | To be used in Global Slowdown scenario
| Neutral | AEMO assumptions | [19 empty] | Extrapolated
| Generator | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Bairnsdale | 9.475 | 8.9841 | 9.5157 | 9.6558 | 9.5189 | 10.0494 | 10.5664 | 10.7813 | 11.1783 | 11.4779 | 11.9204 | 12.3162 | 12.2085 | 12.1289 | 12.0423 | 11.9401 | 11.9535 | 12.0239 | 12.019 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
| Barcaldine | 8.885 | 8.3941 | 8.9257 | 9.0658 | 8.9289 | 9.4594 | 9.9764 | 10.1913 | 10.5883 | 10.8879 | 11.3304 | 11.7262 | 11.6185 | 11.5389 | 11.4523 | 11.3501 | 11.3635 | 11.4339 | 11.429 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41
| Bell Bay Three | 10.425 | 9.9341 | 10.4657 | 10.6058 | 10.4689 | 10.9994 | 11.5164 | 11.7313 | 12.1283 | 12.4279 | 12.8704 | 13.2662 | 13.1585 | 13.0789 | 12.9923 | 12.8901 | 12.9035 | 12.9739 | 12.969 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95
| Braemar | 8.885 | 8.3941 | 8.9257 | 9.0658 | 8.9289 | 9.4594 | 9.9764 | 10.1913 | 10.5883 | 10.8879 | 11.3304 | 11.7262 | 11.6185 | 11.5389 | 11.4523 | 11.3501 | 11.3635 | 11.4339 | 11.429 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41
| Braemar 2 | 8.885 | 8.3941 | 8.9257 | 9.0658 | 8.9289 | 9.4594 | 9.9764 | 10.1913 | 10.5883 | 10.8879 | 11.3304 | 11.7262 | 11.6185 | 11.5389 | 11.4523 | 11.3501 | 11.3635 | 11.4339 | 11.429 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41 | 11.41
| Colongra | 9.995 | 9.5041 | 10.0357 | 10.1758 | 10.0389 | 10.5694 | 11.0864 | 11.3013 | 11.6983 | 11.9979 | 12.4404 | 12.8362 | 12.7285 | 12.6489 | 12.5623 | 12.4601 | 12.4735 | 12.5439 | 12.539 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52
| Condamine | 9.185 | 8.6941 | 9.2257 | 9.3658 | 9.2289 | 9.7594 | 10.2764 | 10.4913 | 10.8883 | 11.1879 | 11.6304 | 12.0262 | 11.9185 | 11.8389 | 11.7523 | 11.6501 | 11.6635 | 11.7339 | 11.729 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71
| Darling Downs | 8.685 | 8.1941 | 8.7257 | 8.8658 | 8.7289 | 9.2594 | 9.7764 | 9.9913 | 10.3883 | 10.6879 | 11.1304 | 11.5262 | 11.4185 | 11.3389 | 11.2523 | 11.1501 | 11.1635 | 11.2339 | 11.229 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21
| Dry Creek | 9.655 | 9.1641 | 9.6957 | 9.8358 | 9.6989 | 10.2294 | 10.7464 | 10.9613 | 11.3583 | 11.6579 | 12.1004 | 12.4962 | 12.3885 | 12.3089 | 12.2223 | 12.1201 | 12.1335 | 12.2039 | 12.199 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18
| Hallett | 9.655 | 9.1641 | 9.6957 | 9.8358 | 9.6989 | 10.2294 | 10.7464 | 10.9613 | 11.3583 | 11.6579 | 12.1004 | 12.4962 | 12.3885 | 12.3089 | 12.2223 | 12.1201 | 12.1335 | 12.2039 | 12.199 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18
| Jeeralang | 8.975 | 8.4841 | 9.0157 | 9.1558 | 9.0189 | 9.5494 | 10.0664 | 10.2813 | 10.6783 | 10.9779 | 11.4204 | 11.8162 | 11.7085 | 11.6289 | 11.5423 | 11.4401 | 11.4535 | 11.5239 | 11.519 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
| Ladbroke Grove | 9.655 | 9.1641 | 9.6957 | 9.8358 | 9.6989 | 10.2294 | 10.7464 | 10.9613 | 11.3583 | 11.6579 | 12.1004 | 12.4962 | 12.3885 | 12.3089 | 12.2223 | 12.1201 | 12.1335 | 12.2039 | 12.199 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18
| Laverton North | 9.475 | 8.9841 | 9.5157 | 9.6558 | 9.5189 | 10.0494 | 10.5664 | 10.7813 | 11.1783 | 11.4779 | 11.9204 | 12.3162 | 12.2085 | 12.1289 | 12.0423 | 11.9401 | 11.9535 | 12.0239 | 12.019 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
| Mintaro | 9.655 | 9.1641 | 9.6957 | 9.8358 | 9.6989 | 10.2294 | 10.7464 | 10.9613 | 11.3583 | 11.6579 | 12.1004 | 12.4962 | 12.3885 | 12.3089 | 12.2223 | 12.1201 | 12.1335 | 12.2039 | 12.199 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18
| Mortlake OCGT | 8.775 | 8.2841 | 8.8157 | 8.9558 | 8.8189 | 9.3494 | 9.8664 | 10.0813 | 10.4783 | 10.7779 | 11.2204 | 11.6162 | 11.5085 | 11.4289 | 11.3423 | 11.2401 | 11.2535 | 11.3239 | 11.319 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3
| Newport | 9.475 | 8.9841 | 9.5157 | 9.6558 | 9.5189 | 10.0494 | 10.5664 | 10.7813 | 11.1783 | 11.4779 | 11.9204 | 12.3162 | 12.2085 | 12.1289 | 12.0423 | 11.9401 | 11.9535 | 12.0239 | 12.019 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
| Oakey | 9.185 | 8.6941 | 9.2257 | 9.3658 | 9.2289 | 9.7594 | 10.2764 | 10.4913 | 10.8883 | 11.1879 | 11.6304 | 12.0262 | 11.9185 | 11.8389 | 11.7523 | 11.6501 | 11.6635 | 11.7339 | 11.729 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71
| Osborne | 8.655 | 8.1641 | 8.6957 | 8.8358 | 8.6989 | 9.2294 | 9.7464 | 9.9613 | 10.3583 | 10.6579 | 11.1004 | 11.4962 | 11.3885 | 11.3089 | 11.2223 | 11.1201 | 11.1335 | 11.2039 | 11.199 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18 | 11.18
| Pelican Point | 9.155 | 8.6641 | 9.1957 | 9.3358 | 9.1989 | 9.7294 | 10.2464 | 10.4613 | 10.8583 | 11.1579 | 11.6004 | 11.9962 | 11.8885 | 11.8089 | 11.7223 | 11.6201 | 11.6335 | 11.7039 | 11.699 | 11.68 | 11.68 | 11.68 | 11.68 | 11.68 | 11.68 | 11.68 | 11.68 | 11.68 | 11.68 | 11.68
| Quarantine | 9.405 | 8.9141 | 9.4457 | 9.5858 | 9.4489 | 9.9794 | 10.4964 | 10.7113 | 11.1083 | 11.4079 | 11.8504 | 12.2462 | 12.1385 | 12.0589 | 11.9723 | 11.8701 | 11.8835 | 11.9539 | 11.949 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93 | 11.93
| Roma | 9.185 | 8.6941 | 9.2257 | 9.3658 | 9.2289 | 9.7594 | 10.2764 | 10.4913 | 10.8883 | 11.1879 | 11.6304 | 12.0262 | 11.9185 | 11.8389 | 11.7523 | 11.6501 | 11.6635 | 11.7339 | 11.729 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71
| Smithfield | 9.995 | 9.5041 | 10.0357 | 10.1758 | 10.0389 | 10.5694 | 11.0864 | 11.3013 | 11.6983 | 11.9979 | 12.4404 | 12.8362 | 12.7285 | 12.6489 | 12.5623 | 12.4601 | 12.4735 | 12.5439 | 12.539 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52 | 12.52
| Somerton | 9.475 | 8.9841 | 9.5157 | 9.6558 | 9.5189 | 10.0494 | 10.5664 | 10.7813 | 11.1783 | 11.4779 | 11.9204 | 12.3162 | 12.2085 | 12.1289 | 12.0423 | 11.9401 | 11.9535 | 12.0239 | 12.019 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
| Swanbank E | 9.185 | 8.6941 | 9.2257 | 9.3658 | 9.2289 | 9.7594 | 10.2764 | 10.4913 | 10.8883 | 11.1879 | 11.6304 | 12.0262 | 11.9185 | 11.8389 | 11.7523 | 11.6501 | 11.6635 | 11.7339 | 11.729 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71 | 11.71
| Tallawarra | 9.495 | 9.0041 | 9.5357 | 9.6758 | 9.5389 | 10.0694 | 10.5864 | 10.8013 | 11.1983 | 11.4979 | 11.9404 | 12.3362 | 12.2285 | 12.1489 | 12.0623 | 11.9601 | 11.9735 | 12.0439 | 12.039 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02
| Tamar Valley | 10.425 | 9.9341 | 10.4657 | 10.6058 | 10.4689 | 10.9994 | 11.5164 | 11.7313 | 12.1283 | 12.4279 | 12.8704 | 13.2662 | 13.1585 | 13.0789 | 12.9923 | 12.8901 | 12.9035 | 12.9739 | 12.969 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95 | 12.95
| Torrens Island | 9.655 | 9.1641 | 9.6957 | 9.8358 | 9.6989 | 10.2294 | 10.7464 | 10.9613 | 11.3583 | 11.6579 | 12.1004 | 12.4962 | 12.3885 | 12.3089 | 12.2223 | 12.1201 | 12.1335 | 12.2039 | 12.199 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18
| Townsville | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| Uranquinty | 9.745 | 9.2541 | 9.7857 | 9.9258 | 9.7889 | 10.3194 | 10.8364 | 11.0513 | 11.4483 | 11.7479 | 12.1904 | 12.5862 | 12.4785 | 12.3989 | 12.3123 | 12.2101 | 12.2235 | 12.2939 | 12.289 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27 | 12.27
| Valley Power | 9.475 | 8.9841 | 9.5157 | 9.6558 | 9.5189 | 10.0494 | 10.5664 | 10.7813 | 11.1783 | 11.4779 | 11.9204 | 12.3162 | 12.2085 | 12.1289 | 12.0423 | 11.9401 | 11.9535 | 12.0239 | 12.019 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
| Yarwun | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
| QLD new OCGT | 10.185 | 9.6941 | 10.2257 | 10.3658 | 10.2289 | 10.7594 | 11.2764 | 11.4913 | 11.8883 | 12.1879 | 12.6304 | 13.0262 | 12.9185 | 12.8389 | 12.7523 | 12.6501 | 12.6635 | 12.7339 | 12.729 | 12.71 | 12.71 | 12.71 | 12.71 | 12.71 | 12.71 | 12.71 | 12.71 | 12.71 | 12.71 | 12.71
| NSW new OCGT | 10.995 | 10.5041 | 11.0357 | 11.1758 | 11.0389 | 11.5694 | 12.0864 | 12.3013 | 12.6983 | 12.9979 | 13.4404 | 13.8362 | 13.7285 | 13.6489 | 13.5623 | 13.4601 | 13.4735 | 13.5439 | 13.539 | 13.52 | 13.52 | 13.52 | 13.52 | 13.52 | 13.52 | 13.52 | 13.52 | 13.52 | 13.52 | 13.52
| VIC new OCGT | 10.475 | 9.9841 | 10.5157 | 10.6558 | 10.5189 | 11.0494 | 11.5664 | 11.7813 | 12.1783 | 12.4779 | 12.9204 | 13.3162 | 13.2085 | 13.1289 | 13.0423 | 12.9401 | 12.9535 | 13.0239 | 13.019 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
| SA new OCGT | 10.655 | 10.1641 | 10.6957 | 10.8358 | 10.6989 | 11.2294 | 11.7464 | 11.9613 | 12.3583 | 12.6579 | 13.1004 | 13.4962 | 13.3885 | 13.3089 | 13.2223 | 13.1201 | 13.1335 | 13.2039 | 13.199 | 13.18 | 13.18 | 13.18 | 13.18 | 13.18 | 13.18 | 13.18 | 13.18 | 13.18 | 13.18 | 13.18
| TAS new OCGT | 11.125 | 10.6341 | 11.1657 | 11.3058 | 11.1689 | 11.6994 | 12.2164 | 12.4313 | 12.8283 | 13.1279 | 13.5704 | 13.9662 | 13.8585 | 13.7789 | 13.6923 | 13.5901 | 13.6035 | 13.6739 | 13.669 | 13.65 | 13.65 | 13.65 | 13.65 | 13.65 | 13.65 | 13.65 | 13.65 | 13.65 | 13.65 | 13.65
| QLD new CCGT | 8.685 | 8.1941 | 8.7257 | 8.8658 | 8.7289 | 9.2594 | 9.7764 | 9.9913 | 10.3883 | 10.6879 | 11.1304 | 11.5262 | 11.4185 | 11.3389 | 11.2523 | 11.1501 | 11.1635 | 11.2339 | 11.229 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21 | 11.21
| NSW new CCGT | 9.495 | 9.0041 | 9.5357 | 9.6758 | 9.5389 | 10.0694 | 10.5864 | 10.8013 | 11.1983 | 11.4979 | 11.9404 | 12.3362 | 12.2285 | 12.1489 | 12.0623 | 11.9601 | 11.9735 | 12.0439 | 12.039 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02 | 12.02
| VIC new CCGT | 8.975 | 8.4841 | 9.0157 | 9.1558 | 9.0189 | 9.5494 | 10.0664 | 10.2813 | 10.6783 | 10.9779 | 11.4204 | 11.8162 | 11.7085 | 11.6289 | 11.5423 | 11.4401 | 11.4535 | 11.5239 | 11.519 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
| SA new CCGT | 9.655 | 9.1641 | 9.6957 | 9.8358 | 9.6989 | 10.2294 | 10.7464 | 10.9613 | 11.3583 | 11.6579 | 12.1004 | 12.4962 | 12.3885 | 12.3089 | 12.2223 | 12.1201 | 12.1335 | 12.2039 | 12.199 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18 | 12.18
| TAS new CCGT | 10.625 | 10.1341 | 10.6657 | 10.8058 | 10.6689 | 11.1994 | 11.7164 | 11.9313 | 12.3283 | 12.6279 | 13.0704 | 13.4662 | 13.3585 | 13.2789 | 13.1923 | 13.0901 | 13.1035 | 13.1739 | 13.169 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15 | 13.15
| Fast Change | AEMO assumptions 2020-21: AEMO assumptions; Extrapolated 2040-41: Extrapolated
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Bairnsdale | 9.475 | 8.9841 | 9.4606 | 9.6007 | 9.5189 | 9.9908 | 10.4475 | 10.6594 | 11.0509 | 11.2823 | 11.6486 | 11.9661 | 11.7946 | 11.6536 | 11.5067 | 11.41 | 11.3603 | 11.3645 | 11.3599 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421
| Barcaldine | 8.685 | 8.1941 | 8.6706 | 8.8107 | 8.7289 | 9.2008 | 9.6575 | 9.8694 | 10.2609 | 10.4923 | 10.8586 | 11.1761 | 11.0046 | 10.8636 | 10.7167 | 10.62 | 10.5703 | 10.5745 | 10.5699 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521
| Bell Bay Three | 10.725 | 10.2341 | 10.7106 | 10.8507 | 10.7689 | 11.2408 | 11.6975 | 11.9094 | 12.3009 | 12.5323 | 12.8986 | 13.2161 | 13.0446 | 12.9036 | 12.7567 | 12.66 | 12.6103 | 12.6145 | 12.6099 | 12.5921 | 12.5921 | 12.5921 | 12.5921 | 12.5921 | 12.5921 | 12.5921 | 12.5921 | 12.5921 | 12.5921 | 12.5921
| Braemar | 8.685 | 8.1941 | 8.6706 | 8.8107 | 8.7289 | 9.2008 | 9.6575 | 9.8694 | 10.2609 | 10.4923 | 10.8586 | 11.1761 | 11.0046 | 10.8636 | 10.7167 | 10.62 | 10.5703 | 10.5745 | 10.5699 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521
| Braemar 2 | 8.685 | 8.1941 | 8.6706 | 8.8107 | 8.7289 | 9.2008 | 9.6575 | 9.8694 | 10.2609 | 10.4923 | 10.8586 | 11.1761 | 11.0046 | 10.8636 | 10.7167 | 10.62 | 10.5703 | 10.5745 | 10.5699 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521
| Colongra | 9.995 | 9.5041 | 9.9806 | 10.1207 | 10.0389 | 10.5108 | 10.9675 | 11.1794 | 11.5709 | 11.8023 | 12.1686 | 12.4861 | 12.3146 | 12.1736 | 12.0267 | 11.93 | 11.8803 | 11.8845 | 11.8799 | 11.8621 | 11.8621 | 11.8621 | 11.8621 | 11.8621 | 11.8621 | 11.8621 | 11.8621 | 11.8621 | 11.8621 | 11.8621
| Condamine | 9.185 | 8.6941 | 9.1706 | 9.3107 | 9.2289 | 9.7008 | 10.1575 | 10.3694 | 10.7609 | 10.9923 | 11.3586 | 11.6761 | 11.5046 | 11.3636 | 11.2167 | 11.12 | 11.0703 | 11.0745 | 11.0699 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521
| Darling Downs | 8.485 | 7.9941 | 8.4706 | 8.6107 | 8.5289 | 9.0008 | 9.4575 | 9.6694 | 10.0609 | 10.2923 | 10.6586 | 10.9761 | 10.8046 | 10.6636 | 10.5167 | 10.42 | 10.3703 | 10.3745 | 10.3699 | 10.3521 | 10.3521 | 10.3521 | 10.3521 | 10.3521 | 10.3521 | 10.3521 | 10.3521 | 10.3521 | 10.3521 | 10.3521
| Dry Creek | 9.655 | 9.1641 | 9.6406 | 9.7807 | 9.6989 | 10.1708 | 10.6275 | 10.8394 | 11.2309 | 11.4623 | 11.8286 | 12.1461 | 11.9746 | 11.8336 | 11.6867 | 11.59 | 11.5403 | 11.5445 | 11.5399 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221
| Hallett | 9.655 | 9.1641 | 9.6406 | 9.7807 | 9.6989 | 10.1708 | 10.6275 | 10.8394 | 11.2309 | 11.4623 | 11.8286 | 12.1461 | 11.9746 | 11.8336 | 11.6867 | 11.59 | 11.5403 | 11.5445 | 11.5399 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221
| Jeeralang | 8.975 | 8.4841 | 8.9606 | 9.1007 | 9.0189 | 9.4908 | 9.9475 | 10.1594 | 10.5509 | 10.7823 | 11.1486 | 11.4661 | 11.2946 | 11.1536 | 11.0067 | 10.91 | 10.8603 | 10.8645 | 10.8599 | 10.8421 | 10.8421 | 10.8421 | 10.8421 | 10.8421 | 10.8421 | 10.8421 | 10.8421 | 10.8421 | 10.8421 | 10.8421
| Ladbroke Grove | 9.655 | 9.1641 | 9.6406 | 9.7807 | 9.6989 | 10.1708 | 10.6275 | 10.8394 | 11.2309 | 11.4623 | 11.8286 | 12.1461 | 11.9746 | 11.8336 | 11.6867 | 11.59 | 11.5403 | 11.5445 | 11.5399 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221
| Laverton North | 9.475 | 8.9841 | 9.4606 | 9.6007 | 9.5189 | 9.9908 | 10.4475 | 10.6594 | 11.0509 | 11.2823 | 11.6486 | 11.9661 | 11.7946 | 11.6536 | 11.5067 | 11.41 | 11.3603 | 11.3645 | 11.3599 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421
| Mintaro | 9.655 | 9.1641 | 9.6406 | 9.7807 | 9.6989 | 10.1708 | 10.6275 | 10.8394 | 11.2309 | 11.4623 | 11.8286 | 12.1461 | 11.9746 | 11.8336 | 11.6867 | 11.59 | 11.5403 | 11.5445 | 11.5399 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221
| Mortlake OCGT | 8.775 | 8.2841 | 8.7606 | 8.9007 | 8.8189 | 9.2908 | 9.7475 | 9.9594 | 10.3509 | 10.5823 | 10.9486 | 11.2661 | 11.0946 | 10.9536 | 10.8067 | 10.71 | 10.6603 | 10.6645 | 10.6599 | 10.6421 | 10.6421 | 10.6421 | 10.6421 | 10.6421 | 10.6421 | 10.6421 | 10.6421 | 10.6421 | 10.6421 | 10.6421
| Newport | 9.475 | 8.9841 | 9.4606 | 9.6007 | 9.5189 | 9.9908 | 10.4475 | 10.6594 | 11.0509 | 11.2823 | 11.6486 | 11.9661 | 11.7946 | 11.6536 | 11.5067 | 11.41 | 11.3603 | 11.3645 | 11.3599 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421
| Oakey | 9.185 | 8.6941 | 9.1706 | 9.3107 | 9.2289 | 9.7008 | 10.1575 | 10.3694 | 10.7609 | 10.9923 | 11.3586 | 11.6761 | 11.5046 | 11.3636 | 11.2167 | 11.12 | 11.0703 | 11.0745 | 11.0699 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521
| Osborne | 8.655 | 8.1641 | 8.6406 | 8.7807 | 8.6989 | 9.1708 | 9.6275 | 9.8394 | 10.2309 | 10.4623 | 10.8286 | 11.1461 | 10.9746 | 10.8336 | 10.6867 | 10.59 | 10.5403 | 10.5445 | 10.5399 | 10.5221 | 10.5221 | 10.5221 | 10.5221 | 10.5221 | 10.5221 | 10.5221 | 10.5221 | 10.5221 | 10.5221 | 10.5221
| Pelican Point | 9.155 | 8.6641 | 9.1406 | 9.2807 | 9.1989 | 9.6708 | 10.1275 | 10.3394 | 10.7309 | 10.9623 | 11.3286 | 11.6461 | 11.4746 | 11.3336 | 11.1867 | 11.09 | 11.0403 | 11.0445 | 11.0399 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221
| Quarantine | 9.405 | 8.9141 | 9.3906 | 9.5307 | 9.4489 | 9.9208 | 10.3775 | 10.5894 | 10.9809 | 11.2123 | 11.5786 | 11.8961 | 11.7246 | 11.5836 | 11.4367 | 11.34 | 11.2903 | 11.2945 | 11.2899 | 11.2721 | 11.2721 | 11.2721 | 11.2721 | 11.2721 | 11.2721 | 11.2721 | 11.2721 | 11.2721 | 11.2721 | 11.2721
| Roma | 9.185 | 8.6941 | 9.1706 | 9.3107 | 9.2289 | 9.7008 | 10.1575 | 10.3694 | 10.7609 | 10.9923 | 11.3586 | 11.6761 | 11.5046 | 11.3636 | 11.2167 | 11.12 | 11.0703 | 11.0745 | 11.0699 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521
| Smithfield | 10.495 | 10.0041 | 10.4806 | 10.6207 | 10.5389 | 11.0108 | 11.4675 | 11.6794 | 12.0709 | 12.3023 | 12.6686 | 12.9861 | 12.8146 | 12.6736 | 12.5267 | 12.43 | 12.3803 | 12.3845 | 12.3799 | 12.3621 | 12.3621 | 12.3621 | 12.3621 | 12.3621 | 12.3621 | 12.3621 | 12.3621 | 12.3621 | 12.3621 | 12.3621
| Somerton | 9.475 | 8.9841 | 9.4606 | 9.6007 | 9.5189 | 9.9908 | 10.4475 | 10.6594 | 11.0509 | 11.2823 | 11.6486 | 11.9661 | 11.7946 | 11.6536 | 11.5067 | 11.41 | 11.3603 | 11.3645 | 11.3599 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421
| Swanbank E | 9.185 | 8.6941 | 9.1706 | 9.3107 | 9.2289 | 9.7008 | 10.1575 | 10.3694 | 10.7609 | 10.9923 | 11.3586 | 11.6761 | 11.5046 | 11.3636 | 11.2167 | 11.12 | 11.0703 | 11.0745 | 11.0699 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521 | 11.0521
| Tallawarra | 9.745 | 9.2541 | 9.7306 | 9.8707 | 9.7889 | 10.2608 | 10.7175 | 10.9294 | 11.3209 | 11.5523 | 11.9186 | 12.2361 | 12.0646 | 11.9236 | 11.7767 | 11.68 | 11.6303 | 11.6345 | 11.6299 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121
| Tamar Valley | 10.425 | 9.9341 | 10.4106 | 10.5507 | 10.4689 | 10.9408 | 11.3975 | 11.6094 | 12.0009 | 12.2323 | 12.5986 | 12.9161 | 12.7446 | 12.6036 | 12.4567 | 12.36 | 12.3103 | 12.3145 | 12.3099 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921
| Torrens Island | 9.655 | 9.1641 | 9.6406 | 9.7807 | 9.6989 | 10.1708 | 10.6275 | 10.8394 | 11.2309 | 11.4623 | 11.8286 | 12.1461 | 11.9746 | 11.8336 | 11.6867 | 11.59 | 11.5403 | 11.5445 | 11.5399 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221
| Townsville | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
| Uranquinty | 9.745 | 9.2541 | 9.7306 | 9.8707 | 9.7889 | 10.2608 | 10.7175 | 10.9294 | 11.3209 | 11.5523 | 11.9186 | 12.2361 | 12.0646 | 11.9236 | 11.7767 | 11.68 | 11.6303 | 11.6345 | 11.6299 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121 | 11.6121
| Valley Power | 9.475 | 8.9841 | 9.4606 | 9.6007 | 9.5189 | 9.9908 | 10.4475 | 10.6594 | 11.0509 | 11.2823 | 11.6486 | 11.9661 | 11.7946 | 11.6536 | 11.5067 | 11.41 | 11.3603 | 11.3645 | 11.3599 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421 | 11.3421
| Yarwun | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
| QLD new OCGT | 10.185 | 9.6941 | 10.1706 | 10.3107 | 10.2289 | 10.7008 | 11.1575 | 11.3694 | 11.7609 | 11.9923 | 12.3586 | 12.6761 | 12.5046 | 12.3636 | 12.2167 | 12.12 | 12.0703 | 12.0745 | 12.0699 | 12.0521 | 12.0521 | 12.0521 | 12.0521 | 12.0521 | 12.0521 | 12.0521 | 12.0521 | 12.0521 | 12.0521 | 12.0521
| NSW new OCGT | 10.995 | 10.5041 | 10.9806 | 11.1207 | 11.0389 | 11.5108 | 11.9675 | 12.1794 | 12.5709 | 12.8023 | 13.1686 | 13.4861 | 13.3146 | 13.1736 | 13.0267 | 12.93 | 12.8803 | 12.8845 | 12.8799 | 12.8621 | 12.8621 | 12.8621 | 12.8621 | 12.8621 | 12.8621 | 12.8621 | 12.8621 | 12.8621 | 12.8621 | 12.8621
| VIC new OCGT | 10.475 | 9.9841 | 10.4606 | 10.6007 | 10.5189 | 10.9908 | 11.4475 | 11.6594 | 12.0509 | 12.2823 | 12.6486 | 12.9661 | 12.7946 | 12.6536 | 12.5067 | 12.41 | 12.3603 | 12.3645 | 12.3599 | 12.3421 | 12.3421 | 12.3421 | 12.3421 | 12.3421 | 12.3421 | 12.3421 | 12.3421 | 12.3421 | 12.3421 | 12.3421
| SA new OCGT | 10.655 | 10.1641 | 10.6406 | 10.7807 | 10.6989 | 11.1708 | 11.6275 | 11.8394 | 12.2309 | 12.4623 | 12.8286 | 13.1461 | 12.9746 | 12.8336 | 12.6867 | 12.59 | 12.5403 | 12.5445 | 12.5399 | 12.5221 | 12.5221 | 12.5221 | 12.5221 | 12.5221 | 12.5221 | 12.5221 | 12.5221 | 12.5221 | 12.5221 | 12.5221
| TAS new OCGT | 10.425 | 9.9341 | 10.4106 | 10.5507 | 10.4689 | 10.9408 | 11.3975 | 11.6094 | 12.0009 | 12.2323 | 12.5986 | 12.9161 | 12.7446 | 12.6036 | 12.4567 | 12.36 | 12.3103 | 12.3145 | 12.3099 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921
| QLD new CCGT | 8.685 | 8.1941 | 8.6706 | 8.8107 | 8.7289 | 9.2008 | 9.6575 | 9.8694 | 10.2609 | 10.4923 | 10.8586 | 11.1761 | 11.0046 | 10.8636 | 10.7167 | 10.62 | 10.5703 | 10.5745 | 10.5699 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521 | 10.5521
| NSW new CCGT | 9.495 | 9.0041 | 9.4806 | 9.6207 | 9.5389 | 10.0108 | 10.4675 | 10.6794 | 11.0709 | 11.3023 | 11.6686 | 11.9861 | 11.8146 | 11.6736 | 11.5267 | 11.43 | 11.3803 | 11.3845 | 11.3799 | 11.3621 | 11.3621 | 11.3621 | 11.3621 | 11.3621 | 11.3621 | 11.3621 | 11.3621 | 11.3621 | 11.3621 | 11.3621
| VIC new CCGT | 9.175 | 8.6841 | 9.1606 | 9.3007 | 9.2189 | 9.6908 | 10.1475 | 10.3594 | 10.7509 | 10.9823 | 11.3486 | 11.6661 | 11.4946 | 11.3536 | 11.2067 | 11.11 | 11.0603 | 11.0645 | 11.0599 | 11.0421 | 11.0421 | 11.0421 | 11.0421 | 11.0421 | 11.0421 | 11.0421 | 11.0421 | 11.0421 | 11.0421 | 11.0421
| SA new CCGT | 9.655 | 9.1641 | 9.6406 | 9.7807 | 9.6989 | 10.1708 | 10.6275 | 10.8394 | 11.2309 | 11.4623 | 11.8286 | 12.1461 | 11.9746 | 11.8336 | 11.6867 | 11.59 | 11.5403 | 11.5445 | 11.5399 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221 | 11.5221
| TAS new CCGT | 10.425 | 9.9341 | 10.4106 | 10.5507 | 10.4689 | 10.9408 | 11.3975 | 11.6094 | 12.0009 | 12.2323 | 12.5986 | 12.9161 | 12.7446 | 12.6036 | 12.4567 | 12.36 | 12.3103 | 12.3145 | 12.3099 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921 | 12.2921
| Slow Change | AEMO assumptions 2020-21: AEMO assumptions; Extrapolated 2040-41: Extrapolated
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Bairnsdale | 8.5 | 8.5 | 8.75 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Barcaldine | 7.71 | 7.71 | 7.96 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21
| Bell Bay Three | 9.45 | 9.45 | 9.7 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95
| Braemar | 7.71 | 7.71 | 7.96 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21
| Braemar 2 | 7.71 | 7.71 | 7.96 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21
| Colongra | 9.02 | 9.02 | 9.27 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
| Condamine | 7.96 | 7.96 | 8.21 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46
| Darling Downs | 7.51 | 7.51 | 7.76 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01
| Dry Creek | 8.68 | 8.68 | 8.93 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18
| Hallett | 8.68 | 8.68 | 8.93 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18
| Jeeralang | 8 | 8 | 8.25 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
| Ladbroke Grove | 8.68 | 8.68 | 8.93 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18
| Laverton North | 8.5 | 8.5 | 8.75 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Mintaro | 8.68 | 8.68 | 8.93 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18
| Mortlake OCGT | 7.8 | 7.8 | 8.05 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3
| Newport | 8.5 | 8.5 | 8.75 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Oakey | 8.21 | 8.21 | 8.46 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71
| Osborne | 7.68 | 7.68 | 7.93 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18
| Pelican Point | 8.18 | 8.18 | 8.43 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68
| Quarantine | 8.43 | 8.43 | 8.68 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93
| Roma | 8.21 | 8.21 | 8.46 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71
| Smithfield | 9.02 | 9.02 | 9.27 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
| Somerton | 8.5 | 8.5 | 8.75 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Swanbank E | 8.21 | 8.21 | 8.46 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71
| Tallawarra | 8.52 | 8.52 | 8.77 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02
| Tamar Valley | 9.45 | 9.45 | 9.7 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95
| Torrens Island | 8.68 | 8.68 | 8.93 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18
| Townsville | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
| Uranquinty | 8.77 | 8.77 | 9.02 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27
| Valley Power | 8.5 | 8.5 | 8.75 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Yarwun | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| QLD new OCGT | 8.71 | 8.71 | 8.96 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21
| NSW new OCGT | 9.52 | 9.52 | 9.77 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02
| VIC new OCGT | 9 | 9 | 9.25 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
| SA new OCGT | 9.18 | 9.18 | 9.43 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68
| TAS new OCGT | 9.45 | 9.45 | 9.7 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95
| QLD new CCGT | 7.71 | 7.71 | 7.96 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21
| NSW new CCGT | 8.52 | 8.52 | 8.77 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02
| VIC new CCGT | 8 | 8 | 8.25 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
| SA new CCGT | 8.18 | 8.18 | 8.43 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68
| TAS new CCGT | 9.45 | 9.45 | 9.7 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95
|  | AEMO assumptions | [19 empty] | Extrapolated
| Liquid fuel price | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Liquid fuel | 36.31 | 35.75 | 35.19 | 34.68 | 34.2 | 33.76 | 33.37 | 33.03 | 32.68 | 32.34 | 32.03 | 31.75 | 31.49 | 31.25 | 31.03 | 30.81 | 30.6 | 30.39 | 30.19 | 29.99 | 29.99 | 29.99 | 29.99 | 29.99 | 29.99 | 29.99 | 29.99 | 29.99 | 29.99 | 29.99

## Coal and Biomass price
TOC
Coal prices ($/GJ) real June 2019 dollars
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Existing generators: 2016 Wood Mackenzie Coal Cost Report New entrants: Resources and Energy Quarterly (June 2018) report, Department of Industry, Innovation and Science (AEMO conversions).
|  | AEMO assumptions | [20 empty] | Extrapolated
| Generator | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Bayswater | 1.7527 | 1.7732 | 1.8347 | 1.886 | 1.9577 | 1.9577 | 2.1525 | 2.583 | 2.8597 | 3.0032 | 3.116 | 3.157 | 3.2082 | 3.2595 | 3.3415 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825
| Eraring | 3.0545 | 3.1262 | 3.1775 | 3.2595 | 3.4235 | 3.567 | 3.5977 | 3.7002 | 3.8335 | 3.977 | 4.0693 | 4.1307 | 4.2025 | 4.2742 | 4.3767 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428
| Liddell | 1.7527 | 1.7732 | 1.8347 | 1.886 | 1.9577 | 1.9577 | 2.1525 | 2.583 | 2.8597 | 3.0032 | 3.116 | 3.157 | 3.2082 | 3.2595 | 3.3415 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825
| Mount Piper | 2.583 | 2.6342 | 2.706 | 2.7675 | 2.9212 | 3.034 | 3.1262 | 3.28 | 3.4132 | 3.567 | 3.69 | 3.7515 | 3.7925 | 3.8437 | 3.9257 | 3.9872 | 3.9872 | 3.9872 | 3.9872 | 3.9872 | 3.9872 | 3.9872 | 3.9872 | 3.9872 | 3.9872 | 3.9872 | 3.9872 | 3.9872 | 3.9872 | 3.9872
| Vales Point | 2.952 | 3.0135 | 3.1775 | 3.2595 | 3.4235 | 3.567 | 3.5977 | 3.7002 | 3.8335 | 3.977 | 4.0693 | 4.1307 | 4.2025 | 4.2742 | 4.3767 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428
| Callide B | 2.2857 | 2.3267 | 2.3472 | 2.3678 | 2.3882 | 2.4395 | 2.4805 | 2.4907 | 2.5215 | 2.5522 | 2.6035 | 2.8802 | 3.1262 | 3.1877 | 3.2697 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107
| Callide Power Plant | 2.2857 | 2.3267 | 2.3472 | 2.3678 | 2.3882 | 2.4395 | 2.4805 | 2.4907 | 2.5215 | 2.5522 | 2.6035 | 2.8802 | 3.1262 | 3.1877 | 3.2697 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107
| Gladstone | 3.0237 | 3.075 | 3.157 | 3.2287 | 3.3927 | 3.526 | 3.5568 | 3.6182 | 3.731 | 3.8847 | 3.9872 | 4.0385 | 4.1 | 4.182 | 4.2742 | 4.3255 | 4.3255 | 4.3255 | 4.3255 | 4.3255 | 4.3255 | 4.3255 | 4.3255 | 4.3255 | 4.3255 | 4.3255 | 4.3255 | 4.3255 | 4.3255 | 4.3255
| Kogan Creek | 1.681 | 1.681 | 1.7015 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722
| Millmerran | 1.394 | 1.394 | 1.4042 | 1.4247 | 1.4247 | 1.4247 | 1.4247 | 1.4247 | 1.4247 | 1.4247 | 1.4247 | 1.4247 | 1.435 | 1.435 | 1.435 | 1.435 | 1.435 | 1.435 | 1.4452 | 1.4452 | 1.4452 | 1.4452 | 1.4452 | 1.4452 | 1.4452 | 1.4452 | 1.4452 | 1.4452 | 1.4452 | 1.4452
| Stanwell | 2.6035 | 2.6342 | 2.665 | 2.6855 | 2.706 | 2.7265 | 2.8905 | 3.28 | 3.5875 | 3.7412 | 3.8745 | 3.9257 | 3.9872 | 4.0488 | 4.1615 | 4.2025 | 4.2025 | 4.2025 | 4.2025 | 4.2025 | 4.2025 | 4.2025 | 4.2025 | 4.2025 | 4.2025 | 4.2025 | 4.2025 | 4.2025 | 4.2025 | 4.2025
| Tarong | 3.0237 | 3.0237 | 3.0442 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648
| Tarong North | 3.0237 | 3.0237 | 3.0442 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648
| Loy Yang A | 0.697 | 0.697 | 0.697 | 0.70725 | 0.70725 | 0.70725 | 0.70725 | 0.7175 | 0.7175 | 0.7175 | 0.72775 | 0.72775 | 0.738 | 0.738 | 0.7585 | 0.7585 | 0.76875 | 0.76875 | 0.779 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925
| Loy Yang B | 0.697 | 0.697 | 0.697 | 0.70725 | 0.70725 | 0.70725 | 0.70725 | 0.7175 | 0.7175 | 0.7175 | 0.72775 | 0.72775 | 0.738 | 0.738 | 0.7585 | 0.7585 | 0.76875 | 0.76875 | 0.779 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925 | 0.78925
| Yallourn | 0.68675 | 0.68675 | 0.697 | 0.697 | 0.697 | 0.697 | 0.70725 | 0.70725 | 0.70725 | 0.7175 | 0.7175 | 0.7175 | 0.72775 | 0.72775 | 0.738 | 0.738 | 0.7585 | 0.7585 | 0.76875 | 0.779 | 0.779 | 0.779 | 0.779 | 0.779 | 0.779 | 0.779 | 0.779 | 0.779 | 0.779 | 0.779

## Fixed OPEX
TOC
Fixed operating cost ($/kW/year) real June 2019 dollars
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Costs that are incurred regardless of energy generated.
| Existing and Committed generators |  | New entrant technologies, after applying regional cost factors
| Generator | Fixed OPEX ($/kW/year) | Generator | Fixed OPEX ($/kW/year)
| Bayswater | 53.2 |  | Vic low | Vic medium | Vic high | Qld low | Qld medium | Qld high | NSW low | NSW medium | NSW high | SA Low | SA medium | SA high | WA low | WA medium | WA high | NT low | NT medium | NT high | Tas low | Tas medium | Tas high
| Eraring | 53.2 | OCGT | 4.2 | 4.326 | 4.41 | 4.494 | 5.04 | 5.628 | 4.746 | 5.124 | 5.544 | 4.242 | 4.746 | 5.25 | 4.536 | 5.418 | 6.3 | 4.998 | 5.964 | 6.972 | 4.41 | 4.788 | 5.166
| Liddell | 53.2 | CCGT | 10.5 | 10.815 | 11.025 | 11.235 | 12.6 | 14.07 | 11.865 | 12.81 | 13.86 | 10.605 | 11.865 | 13.125 | 11.34 | 13.545 | 15.75 | 12.495 | 14.91 | 17.43 | 11.025 | 11.97 | 12.915
| Mount Piper | 53.2 | Large scale Solar PV | 14.44 | 14.8732 | 15.162 | 15.4508 | 17.328 | 19.3496 | 16.3172 | 17.6168 | 19.0608 | 14.5844 | 16.3172 | 18.05 | 15.5952 | 18.6276 | 21.66 | 17.1836 | 20.5048 | 23.9704 | 15.162 | 16.4616 | 17.7612
| Vales Point | 53.2 | Battery Storage (2hrs storage) | 8 | 8.24 | 8.4 | 8.56 | 9.6 | 10.72 | 9.04 | 9.76 | 10.56 | 8.08 | 9.04 | 10 | 8.64 | 10.32 | 12 | 9.52 | 11.36 | 13.28 | 8.4 | 9.12 | 9.84
| Callide B | 53.2 | Wind | 36.02 | 37.1006 | 37.821 | 38.5414 | 43.224 | 48.2668 | 40.7026 | 43.9444 | 47.5464 | 36.3802 | 40.7026 | 45.025 | 38.9016 | 46.4658 | 54.03 | 42.8638 | 51.1484 | 59.7932 | 37.821 | 41.0628 | 44.3046
| Callide Power Plant | 53.2 | Pumped hydro | 16 | 16.48 | 16.8 | 17.12 | 19.2 | 21.44 | 18.08 | 19.52 | 21.12 | 16.16 | 18.08 | 20 | 17.28 | 20.64 | 24 | 19.04 | 22.72 | 26.56 | 16.8 | 18.24 | 19.68
| Gladstone | 53.2
| Kogan Creek | 53.2
| Millmerran | 53.2
| Stanwell | 53.2
| Tarong | 53.2
| Tarong North | 53.2
| Loy Yang A1 | 145.58
| Loy Yang B1 | 115.07
| Yallourn1 | 151.23
| Colongra | 4.2
| Smithfield | 10.5
| Tallawarra | 10.5
| Uranquinty | 4.2
| Barcaldine | 4.2
| Braemar | 4.2
| Condamine | 10.5
| Darling Downs | 10.5
| Oakey | 4.2
| Roma | 4.2
| Swanbank E | 10.5
| Yabulu (Townsville) | 10.5
| Yarwun | 10.5
| Somerton | 4.2
| Bairnsdale | 4.2
| Jeeralang A | 4.2
| Jeeralang B | 4.2
| Laverton North | 4.2
| Mortlake | 4.2
| Newport | 47.1277
| Valley Power | 4.2
| Barker Inlet | 15.12
| Hallett GT | 4.2
| Dry Creek | 4.2
| Ladbroke Grove | 4.2
| Mintaro | 4.2
| Osborne | 10.5
| Pelican Point | 10.5
| Quarantine | 4.2
| Torrens Island A | 47.1277
| Torrens Island B | 47.1277
| Bell Bay Three | 4.2
| Tamar Valley CCGT | 10.5
| Tamar Valley OCGT | 4.2
| Hunter Valley GT | 4.2
| Mackay GT | 4.2
| Mount Stuart | 4.2
| Angaston | 15.12
| Lonsdale | 15.12
| Port Lincoln | 4.2
| Port Lincoln 3 | 4.2
| Port Stanvac | 15.12
| Snuggery | 4.2
| All hydro | 58.25
| All wind | 45.1
| All solar | 25.7
| All batteries | 0
Note: Sourced from GHD with the exception of the brown coal plants, which are from ACIL Allen.

## Variable OPEX
TOC
Variable operating cost ($/MWh) real June 2019 dollars
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Costs that can be expressed in terms of energy generated, not including fuel costs.
| Existing and Committed generators |  | New entrant technologies, after applying regional cost factors
| Generator | Variable OPEX ($/MWh) | Generator | Variable OPEX ($/MWh)
| Bayswater | 4.21 |  | Vic low | Vic medium | Vic high | Qld low | Qld medium | Qld high | NSW low | NSW medium | NSW high | SA Low | SA medium | SA high | WA low | WA medium | WA high | NT low | NT medium | NT high | Tas low | Tas medium | Tas high
| Eraring | 4.21 | OCGT | 10.53 | 10.8459 | 11.0565 | 11.2671 | 12.636 | 14.1102 | 11.8989 | 12.8466 | 13.8996 | 10.6353 | 11.8989 | 13.1625 | 11.3724 | 13.5837 | 15.795 | 12.5307 | 14.9526 | 17.4798 | 11.0565 | 12.0042 | 12.9519
| Liddell | 4.21 | CCGT | 7.37 | 7.5911 | 7.7385 | 7.8859 | 8.844 | 9.8758 | 8.3281 | 8.9914 | 9.7284 | 7.4437 | 8.3281 | 9.2125 | 7.9596 | 9.5073 | 11.055 | 8.7703 | 10.4654 | 12.2342 | 7.7385 | 8.4018 | 9.0651
| Mount Piper | 4.21 | Large scale Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Vales Point | 4.21 | Battery Storage (2hrs storage) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Callide B | 4.21 | Wind | 2.6667 | 2.7467 | 2.8 | 2.8533 | 3.2 | 3.5733 | 3.0133 | 3.2533 | 3.52 | 2.6933 | 3.0133 | 3.3333 | 2.88 | 3.44 | 4 | 3.1733 | 3.7867 | 4.4267 | 2.8 | 3.04 | 3.28
| Callide Power Plant | 4.21 | Pumped hydro | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Gladstone | 4.21
| Kogan Creek | 4.21
| Millmerran | 4.21
| Stanwell | 4.21
| Tarong | 4.21
| Tarong North | 4.21
| Loy Yang A | 4.21
| Loy Yang B | 4.21
| Yallourn | 4.21
| Colongra | 10.53
| Smithfield | 7.37
| Tallawarra | 7.37
| Uranquinty | 10.53
| Barcaldine | 10.53
| Braemar | 10.53
| Condamine | 7.37
| Darling Downs | 7.37
| Oakey | 10.53
| Roma | 10.53
| Swanbank E | 7.37
| Yabulu (Townsville) | 7.37
| Yarwun | 7.37
| Somerton | 10.53
| Bairnsdale | 10.53
| Jeeralang A | 10.53
| Jeeralang B | 10.53
| Laverton North | 10.53
| Mortlake | 10.53
| Newport | 2.3287
| Valley Power | 10.53
| Barker Inlet | 11.18
| Hallett GT | 10.53
| Dry Creek | 10.53
| Ladbroke Grove | 10.53
| Mintaro | 10.53
| Osborne | 7.37
| Pelican Point | 7.37
| Quarantine | 10.53
| Torrens Island A | 2.3287
| Torrens Island B | 2.3287
| Bell Bay Three | 10.53
| Tamar Valley CCGT | 7.37
| Tamar Valley OCGT | 10.53
| Hunter Valley GT | 10.53
| Mackay GT | 10.53
| Mount Stuart | 10.53
| Angaston | 11.18
| Lonsdale | 11.18
| Port Lincoln | 10.53
| Port Lincoln 3 | 10.53
| Port Stanvac | 11.18
| Snuggery | 10.53
| All hydro | 7.19
| All wind | 2.67
| All solar | 0
| All batteries | 0

## Connection cost
TOC
Initial connection costs ($/kW) real June 2019 dollars
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Connection costs increase the build costs of new technologies to cater for transmission infrasturcture to connect to the grid, and varies depending on the proximity to transmission assets
Final connection costs will be subject to modelling outcomes
| Renewable Energy Zone | Wind/Solar | Battery | NEM Region | Gas | Batteries | Pumped hydro
| Far North Queensland | 98.0068 | 10 | QLD | 82.18 | 10 | 98.01
| North Queensland Clean Energy Hub | 111.322 | 10 | NSW | 86.5457 | 10 | 85.51
| Northern Queensland | 98.0068 | 10 | VIC | 73.4587 | 10 | 100.05
| Isaac | 98.0068 | 10 | SA | 82.18 | 10 | 98.01
| Barcaldine | 111.322 | 10 | TAS | 73.4587 | 10 | 100.09
| Fitzroy | 98.0068 | 10
| Darling Downs | 98.0068 | 10
| North West New South Wales | 85.5075 | 10
| New England | 85.5075 | 10
| Central West New South Wales | 85.5075 | 10
| Southern New South Wales Tablelands | 75.5212 | 10
| Cooma-Monaro | 75.5212 | 10
| Tumut | 75.5212 | 10
| South West New South Wales | 85.5075 | 10
| Broken Hill | 108.0433 | 10
| Murray River | 100.0542 | 10
| Western Victoria | 100.0542 | 10
| Moyne | 71.4751 | 10
| Ovens Murray | 100.0542 | 10
| Gippsland | 108.0433 | 10
| South East South Australia | 111.322 | 10
| Riverland | 111.322 | 10
| Mid-North South Australia | 98.0068 | 10
| Yorke Peninsula | 98.0068 | 10
| Northern South Australia | 98.0068 | 10
| Leigh Creek | 111.322 | 10
| Roxby Downs | 111.322 | 10
| Eastern Eyre Peninsula | 111.322 | 10
| Western Eyre Peninsula | 111.322 | 10
| North West Tasmania | 100.0542 | 10
| Tasmania Midlands | 100.0542 | 10
| North East Tasmania | 100.0542 | 10

## Build limits
TOC
Initial build limits (MW)
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Potential in each NEM region to build different thermal and storage capacities; potential in each zone to build new renewable energy capacity
The new renewable energy capacity in each REZ zone will be moderated by transmission expansion choices in each scenario, loss factor impacts, etc
| REZ # | Location | Region | NTNDP zone | Wind generation limits (MW) |  | Solar PV (MW)1 | Pumped Hydro Limits (MW)2 |  | Battery Storage 2hrs (MW) | OCGT (MW) | CCGT (MW) | Transmission-limited total build in the REZ3 | Indicative transmission expansion cost ($M/MW Real 2019)4 | Additional generation capacity available (zero additional cost) in REZs due to the development of interconnectors
[5 empty] | High | Medium | Solar | 6hrs storage | 24hrs storage | [5 empty] | KerangLink | Project EnergyConnect | Marinus Link 600 MW | Marnius Link 1,200 MW | Marinus Link 750 MW | Marinus Link 1,500 MW
| 1 | Far North Queensland | QLD | NQ | 0 | 0 | 0 | [5 empty] | 700 | 1.1787 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | North Queensland Clean Energy Hub | QLD | NQ | 2320 | 6955 | 3982 | [5 empty] | 0 | 1.273 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Northern Queensland | QLD | NQ | 0 | 0 | 1650 | [5 empty] | 2400 (note 5) | 0.88867 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | Isaac | QLD | NQ | 465 | 1395 | 3500 | [5 empty] | 2700 (note 6) | 0.68368 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | Barcaldine | QLD | CQ | 475 | 1435 | 4000 | [5 empty] | 0 | 0.95222 | 0 | 0 | 0 | 0 | 0 | 0
| 6 | Fitzroy | QLD | CQ | 220 | 670 | 2000 | [5 empty] | 2900 (note 7) | 0.5125 | 0 | 0 | 0 | 0 | 0 | 0
| 7 | Darling Downs | QLD | SWQ | 695 | 2090 | 3743 | [5 empty] | 2743 | 0.17117 | 0 | 0 | 0 | 0 | 0 | 0
| 8 | North West New South Wales | NSW | NNS | 200 | 615 | 3250 | [5 empty] | 100 | 0.29212 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | New England | NSW | NNS | 900 | 2760 | 1750 | [5 empty] | 300 | 0.29212 | 0 | 0 | 0 | 0 | 0 | 0
| 10 | Central West New South Wales | NSW | NCEN | 620 | 2265 | 6546.6 | [5 empty] | 0 | 0.29212 | 0 | 0 | 0 | 0 | 0 | 0
| 11 | Southern New South Wales Tablelands | NSW | CAN | 575 | 1735 | 1000 | [5 empty] | 1000 | 0.2296 | 1000 | 0 | 0 | 0 | 0 | 0
| 12 | Cooma-Monaro | NSW | CAN | 0 | 0 | 0 | [5 empty] | 200 | NA (note 8) | 0 | 0 | 0 | 0 | 0 | 0
| 13 | Tumut | NSW | CAN | 0 | 0 | 0 | [5 empty] | 0 | NA (note 8) | 0 | 0 | 0 | 0 | 0 | 0
| 14 | South West New South Wales | NSW | SWNSW | 530 | 1570 | 2142 | [5 empty] | 0 | 0.533 | 1000 | 600 | 0 | 0 | 0 | 0
| 15 | Broken Hill | NSW | SWNSW | 620 | 1870 | 4000 | [5 empty] | 100 | 0.6765 | 0 |  | 0 | 0 | 0 | 0
| 16 | Murray River (VIC) | VIC | CVIC | 530 | 1570 | 2561.13 | [5 empty] | 0 | 0.3854 | 2000 | 380 | 0 | 0 | 0 | 0
| 17 | Western Victoria | VIC | CVIC | 0 | 1042 | 0 | [5 empty] | 450 (note 9) | 0.205 | 1000 | 0 | 0 | 0 | 0 | 0
| 18 | Moyne | VIC | MEL | 0 | 1469.7 | 0 | [5 empty] | 1175 | 0.08815 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | Ovens Murray | VIC | NVIC | 0 | 0 | 0 | [5 empty] | 300 | NA (note 8) | 0 | 0 | 0 | 0 | 0 | 0
| 20 | Gippsland | VIC | LV | 35 | 105 | 0 | [5 empty] | 2000 | NA (note 8) | 0 | 0 | 0 | 0 | 0 | 0
| 21 | South East South Australia | SA | SESA | 455 | 1355 | 0 | [5 empty] | 500 | 0.25625 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | Riverland (NSW) | NSW | SWNSW | 155 | 465 | 2000 | [5 empty] | 0 | 0.533 | 0 | 600 | 0 | 0 | 0 | 0
| 23 | Mid-North South Australia | SA | ADE | 605 | 1820 | 0 | [5 empty] | 1000 | 0.25625 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | Yorke Peninsula | SA | NSA | 155 | 465 | 0 | [5 empty] | 50 | 0.12812 | 0 | 0 | 0 | 0 | 0 | 0
| 25 | Northern South Australia | SA | NSA | 0 | 0 | 1500 | [5 empty] | 1000 (see note 10) | 0.25625 | 0 | 0 | 0 | 0 | 0 | 0
| 26 | Leigh Creek | SA | NSA | 295 | 895 | 3250 | [5 empty] | 10 (see note 10) | 0.5125 | 0 | 0 | 0 | 0 | 0 | 0
| 27 | Roxby Downs | SA | NSA | 0 | 0 | 1700 | [5 empty] | 960 (see note 10) | 0.30032 | 0 | 0 | 0 | 0 | 0 | 0
| 28 | Eastern Eyre Peninsula | SA | NSA | 290 | 870 | 2500 | [5 empty] | 500 (see note 10) | 0.38437 | 0 | 0 | 0 | 0 | 0 | 0
| 29 | Western Eyre Peninsula | SA | NSA | 175 | 540 | 2000 | [5 empty] | 0 (see note 10) | 0.38437 | 0 | 0 | 0 | 0 | 0 | 0
| 30 | North West Tasmania | TAS | TAS | 388.4 | 1500 | 150 (note 11) | [5 empty] | 200 (note 11) | 0.150 (note 11) | 0 | 0 | 800 | 1888 | 800 | 1888
| 31 | Tasmania Midlands | TAS | TAS | 286 | 1300 | 150 (note 11) | [5 empty] | 220 (note 11) | 0.225 (note 11) | 0 | 0 | 540 | 540 | 540 | 540
| 32 | North East Tasmania | TAS | TAS | 300 (note 11) | 900 (note 11) | 50 (note 11) | [5 empty] | 1,250 (note 11) | 0.2296 | 0 | 0 | 0 | 0 | 0 | 0
|  | NSW12 | NSW |  |  |  |  | 3400 | 0 | NA | NA | NA | NA | NA
|  | QLD12 | QLD |  |  |  |  | 1800 | 0 | NA | NA | NA | NA | NA
|  | SA12 | SA |  |  |  |  | 500 | 0 | NA | NA | NA | NA | NA
|  | TAS13 | TAS |  |  |  |  | 0 | 1600 | NA | NA | NA | NA | NA
|  | VIC12 | VIC |  |  |  |  | 1200 | 0 | NA | NA | NA | NA | NA
Notes:
1. Solar build limit determined by an assumed 0.25% of the approximate land area of the Renewable Energy Zones, allowing for typical land area requirements for solar PV, up to 4,000MW per REZ. Applies to both CST and PV.
2. Pumped hydro build limits are based on Entura report
3. Intraregional transmission augmentations may be selected by the model if economic to access larger new renewable resource locations
4. Indicative transmission cost represents indicative network expansion to connect the REZ to the nearest major load centre.
5. 2400 MW includes total build capacity in REZs 1, 2 and 3 in the existing network.
6. 2700 MW includes total build capacity in REZs 1,2,3 and 4 in the existing network.
7. 2900 MW includes total build capacity in REZs 1,2,3, 4, 5 and 6 in the existing network.
8. Available wind and solar resource capacity is less than the existing transmission capacity.
9. Western Victoria RIT-T augmentation included.
10. Existing network can accommodate up to 1600 MW from REZs 25, 26, 27, 28 and 29.
11. Advised by TasNetworks
12. Pumped hydro build limits are based on Entura report in respect to 6 hour storage
13. Pumped hydro build limits are based on Entura report in respect to 24 hour storage

## Capacity Factors
TOC
Capacity Factors
Primary source: AEMO Electricity Statement of Opportunities 2018
Capacity factors are static for all installations. No capacity factor improvement / degradation due to technology improvement / natural reduction in best installation sites, however for wind farms the expected capacity factor improvement through time is reflected in capital cost reductions.
| REZ Name | Region | Wind |  | Solar1
|  |  | High | Medium | Solar PV
| North Queensland Clean Energy Hub | QLD | 48.16% | 38.18% | 30.59%
| Northern Queensland | QLD | - | - | 29.04%
| Barcaldine | QLD | 41.5% | 34.73% | 32.41%
| Isaac | QLD | 46.28% | 34.39% | 30.08%
| Fitzroy | QLD | 45.22% | 35.49% | 29.51%
| Darling Downs | QLD | 44.52% | 38.42% | 29.88%
| North West New South Wales | NSW | 26.79% | 25.04% | 30.11%
| New England | NSW | 37.7% | 37.76% | 29.14%
| Central West New South Wales | NSW | 33.05% | 30.21% | 29.93%
| Southern New South Wales Tablelands | NSW | 42.5% | 40.8% | 26.49%
| Murray River (NSW) | NSW | 31.03% | 29.61% | 28.81%
| Murray River (VIC) | VIC | 31.05% | 29.61% | 28.52%
| Riverland (NSW) | NSW | 30.31% | 29.59% | 28.93%
| Riverland (SA) | SA | 30.32% | 29.65% | 28.38%
| Broken Hill | NSW | 36.28% | 31.96% | 30.85%
| Western Victoria | VIC | - | 33.7% | -
| Moyne | VIC | - | 36.73% | -
| Gippsland | VIC | 30.39% | 30.9% | -
| South East South Australia | SA | 38.17% | 35.94% | -
| Mid-North South Australia | SA | 37% | 37% | -
| Yorke Peninsula | SA | 36.61% | 34.18% | -
| Northern South Australia | SA | - | - | 29.82%
| Leigh Creek | SA | 41.42% | 39.65% | 31.64%
| Roxby Downs | SA | - | - | 31.4%
| Eastern Eyre Peninsula | SA | 36.86% | 36.14% | 27.79%
| Western Eyre Peninsula | SA | 35.87% | 32.28% | 28.55%
| North East Tasmania | TAS | 43.52% | 42.7% | 24.88%
| North West Tasmania | TAS | 47.84% | 42.89% | 22.66%
| Tasmania Midlands | TAS | 51.47% | 44.43% | 24.08%
1. Unlike wind, the solar capacity factors are not strictly based on AEMO 2018 ESOO traces, but instead are based on site-specific solar insolation measurements.

## Lead Time
TOC
Lead time (years)
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Development lead time considers the time necessary to undertake feasibility studies, secure necessary development approvals, and to construct the project. It is assumed that feasibility studies are already underway for these technologies. Therefore, the model is able to build new technologies once the Construction Time has passed. Assumed start date of 1/07/2019. (e.g. new pump hydro capacity can be built from 1/07/2023). This deviates from the AEMO Feb 2019 ISP, where the Total lead time is used and the start date is 1/07/2020.
| Technology | Feasibility Period (years) | Construction Time (years) | Total lead time (years)
| OCGT | 0 | 1 | 1
| CCGT | 3 | 2 | 5
| Large scale Solar PV | 0 | 1 | 1
| Battery storage (2 hrs) | 1 | 1 | 2
| Wind | 0 | 2 | 2
| Pumped hydro | 2 | 4 | 6

## Storage properties
TOC
Storage properties
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
| Property | Value
| Maximum power1 | 1 | MW
| Energy capacity | 2 | MWh
| Charge efficiency (utility) | 81%
| Lifetime | 15 | years
1. Power and capacity are defined as a 1:2 ratio. The model is free to build utility-scale batteries up to defined build limits
Mainland pumped hydro properties
| Property | Value
| Maximum power | 100 | MW
| Energy capacity | 6 | hours
| Pump efficiency | 77.5%
| Lifetime | 50 | years
Tasmanian pumped hydro properties
| Property | Value
| Maximum power | 100 | MW
| Energy capacity | 24 | hours
| Pump efficiency | 77.5%
| Lifetime | 50 | years

## Mainland hydro Inflows
TOC
Mainland hydro storage inflows (GWh)
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Blowering | - | - | - | - | - | - | - | - | 6.3 | 24.6 | 30.7 | 34.3
| Eucumbene | 328 | 330 | 100 | 329 | 434 | 750 | 749 | 434 | 435 | 434 | 154 | 293
Fitzroy Falls | bar: Jan to Dec
| Guthega | 4.6 | 1.6 | 0.3 | 0.8 | 4 | 7.3 | 9.3 | 14.8 | 20.6 | 33.5 | 25.3 | 14.2
| Koombooloomba Dam | 15.6 | 21.5 | 22.6 | 16.8 | 22.5 | 40 | 35.9 | 72.8 | 62.7 | 50.7 | 35.9 | 44.5
| Kuranda Weir | 31.2 | 25.3 | 29.4 | 17 | 28.7 | 27.3 | 17.4 | 12.5 | 30 | 18.5 | 16.3 | 12.6
Split Yard Creek Dam | bar: Jan to Dec
| Eildon | 3.8 | 1.8 | 1.9 | 3.4 | 5.5 | 18.8 | 33.7 | 45.7 | 48.6 | 33.4 | 16.5 | 6.5
| Dartmouth | 10.1 | 7.7 | 4.1 | 5 | 9.7 | 20.9 | 32.1 | 42.7 | 58.8 | 50.8 | 26.4 | 16.7
Note: Hydro storage inflow for the Kiewa scheme (comprising McKay Creek, Bogong, and West Kiewa Power Stations) was not included in the AEMO Feb 2019 assumptions workbook. Therefore an annual inflow of 404 GWh was used, as per: https://www.agl.com.au/about-agl/how-we-source-energy/hydroelectric-assets
| Queensland | Aug: Victoria
Snowy

## Tasmanian hydro Inflows
TOC
Tasmanian hydro storage inflows (GWh)
Primary source: TasNetworks and Hydro Tasmania
| Natural inflows: not inclusive of upstream inflows (GWh) | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| Historical profile | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | 2017-18 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
| Gordon | 1111.24 | 863.47 | 1397.22 | 1154.49 | 1043.88 | 1174.85 | 1249.77 | 1141.54 | 1111.24 | 863.47 | 1397.22 | 1154.49 | 1043.88 | 1174.85 | 1249.77 | 1141.54 | 1111.24 | 863.47 | 1397.22 | 1154.49 | 1043.88 | 1174.85 | 1249.77 | 1141.54 | 1111.24 | 863.47 | 1397.22 | 1154.49 | 1043.88 | 1174.85
| Poatina | 1278.95 | 814.27 | 1649.54 | 936.16 | 1394 | 1462.46 | 1088.37 | 1757.26 | 1278.95 | 814.27 | 1649.54 | 936.16 | 1394 | 1462.46 | 1088.37 | 1757.26 | 1278.95 | 814.27 | 1649.54 | 936.16 | 1394 | 1462.46 | 1088.37 | 1757.26 | 1278.95 | 814.27 | 1649.54 | 936.16 | 1394 | 1462.46
| Trevallyn | 578.16 | 269.63 | 694.46 | 248.93 | 423.6 | 595.8 | 189.66 | 803.08 | 578.16 | 269.63 | 694.46 | 248.93 | 423.6 | 595.8 | 189.66 | 803.08 | 578.16 | 269.63 | 694.46 | 248.93 | 423.6 | 595.8 | 189.66 | 803.08 | 578.16 | 269.63 | 694.46 | 248.93 | 423.6 | 595.8
| John Butters | 571.12 | 515.19 | 734.38 | 609.67 | 552.27 | 653.78 | 695.85 | 602.05 | 571.12 | 515.19 | 734.38 | 609.67 | 552.27 | 653.78 | 695.85 | 602.05 | 571.12 | 515.19 | 734.38 | 609.67 | 552.27 | 653.78 | 695.85 | 602.05 | 571.12 | 515.19 | 734.38 | 609.67 | 552.27 | 653.78
| Tarraleah | 719.44 | 700.91 | 739 | 717.54 | 708.65 | 719.51 | 724.84 | 717.37 | 719.44 | 700.91 | 739 | 717.54 | 708.65 | 719.51 | 724.84 | 717.37 | 719.44 | 700.91 | 739 | 717.54 | 708.65 | 719.51 | 724.84 | 717.37 | 719.44 | 700.91 | 739 | 717.54 | 708.65 | 719.51
| Tungatinah | 747.81 | 506.1 | 924.43 | 624.66 | 615.9 | 778.26 | 723.29 | 764.02 | 747.81 | 506.1 | 924.43 | 624.66 | 615.9 | 778.26 | 723.29 | 764.02 | 747.81 | 506.1 | 924.43 | 624.66 | 615.9 | 778.26 | 723.29 | 764.02 | 747.81 | 506.1 | 924.43 | 624.66 | 615.9 | 778.26
| Lower Derwent | 317.44 | 190.53 | 430.52 | 265.15 | 258.27 | 388.67 | 291.23 | 277.08 | 317.44 | 190.53 | 430.52 | 265.15 | 258.27 | 388.67 | 291.23 | 277.08 | 317.44 | 190.53 | 430.52 | 265.15 | 258.27 | 388.67 | 291.23 | 277.08 | 317.44 | 190.53 | 430.52 | 265.15 | 258.27 | 388.67
| Anthony Pieman | 1792.73 | 1574.8 | 2220.87 | 1760.58 | 1660.49 | 2003.59 | 2031.28 | 1902.28 | 1792.73 | 1574.8 | 2220.87 | 1760.58 | 1660.49 | 2003.59 | 2031.28 | 1902.28 | 1792.73 | 1574.8 | 2220.87 | 1760.58 | 1660.49 | 2003.59 | 2031.28 | 1902.28 | 1792.73 | 1574.8 | 2220.87 | 1760.58 | 1660.49 | 2003.59
| Mersey Forth Upper | 556.77 | 457.73 | 637.5 | 501.75 | 476.92 | 584.51 | 597.47 | 643.67 | 556.77 | 457.73 | 637.5 | 501.75 | 476.92 | 584.51 | 597.47 | 643.67 | 556.77 | 457.73 | 637.5 | 501.75 | 476.92 | 584.51 | 597.47 | 643.67 | 556.77 | 457.73 | 637.5 | 501.75 | 476.92 | 584.51
| Mersey Forth Lower | 558.23 | 439.98 | 638.55 | 465.1 | 469.43 | 571.02 | 552.14 | 678.37 | 558.23 | 439.98 | 638.55 | 465.1 | 469.43 | 571.02 | 552.14 | 678.37 | 558.23 | 439.98 | 638.55 | 465.1 | 469.43 | 571.02 | 552.14 | 678.37 | 558.23 | 439.98 | 638.55 | 465.1 | 469.43 | 571.02
[12 empty] | MerseyForthLower | 678.37 | 558.23 | 439.98 | 638.55 | 465.1 | 469.43 | 571.02 | 552.14

## Prudent storage level
TOC
Prudent Storage Level for Tasmanian Hydro
Primary source: Hydro Tasmania public documents
The whole-of-system reservoir volume is known as Total Energy in Storage and the monthly minimums are the PSL profile that is imposed as part of Tasmania’s energy security plan mandated by the Tasmanian Government to manage the consequences of an extended Basslink outage. Based on a Full Starage Energy of 13,546 GWh (system less Lake Echo). TasNetworks has assumed that with the presence of Marinus Link, the requirement to maintain energy reserves to manage a Basslink outage would be reduced. With Marinus Link, prudent storage levels are reduced to values that existed prior to the Tasmanian Energy Security Taskforce review.
| PSL (GWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| PSL without Marinus Link | 5076 | 4722 | 4362 | 4043 | 3981 | 3956 | 4097 | 4248 | 4764 | 5185 | 5344 | 5212
| PSL without Marinus Link | 3721 | 3367 | 3007 | 2688 | 2626 | 2601 | 2742 | 2893 | 3409 | 3830 | 3989 | 3857
| PSL (% of FSL) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| PSL without Marinus Link | 37.5% | 34.9% | 32.2% | 29.8% | 29.4% | 29.2% | 30.2% | 31.4% | 35.2% | 38.3% | 39.5% | 38.5%
| PSL without Marinus Link | 27.5% | 24.9% | 22.2% | 19.8% | 19.4% | 19.2% | 20.2% | 21.4% | 25.2% | 28.3% | 29.5% | 28.5%

## Storage Initial Level
TOC
Storage initial level
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
| Reservoir | Initial Volume (1000 m³) | Maximum capacity (1000 m³)
| Blowering | 1100667 | 1610000
| Guthega | 739 | 1400
| Koombooloomba Dam | 94427.1 | 184500
| Kuranda Weir | 1179 | 1387
| Jounama Pondage | 5705 | 27800
| Murray Pondage | 5895 | 13100
| Murray 2 Pondage | 677 | 1500
| Talbingo | 113741 | 160400
| Tumut Pondage | 31111 | 50000
| Tumut 2 Pondage | 788 | 1500
| Bendeela Pondage | 343 | 780
| Fitzroy Falls | 711.04 | 880
| Lake Yarrunga | 21600 | 36000
| Split Yard Creek Dam | 4408 | 10018
| Wivenhoe | 1145999 | 1165000
| Anthony-Pieman Pond | 262961 | 294430
| Burbury | 103219 | 233000
| Derwent | 686778 | 1848200
| Great Lake-Trevallyn Pond | 1008330 | 6567000
| Lake Gordon | 103219 | 4699000
| Mersey Forth Pond | 104582 | 227000
| Dartmouth | 3002437 | 3906000
| Eildon | 2176144 | 3387000
| Hume Dam | 1874062 | 3040000

## Interconnector Capability
TOC
Interconnector capability (MW)
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Static maximum transfer limits, expressed as power transferred into the receiving region
| Interconnector | Forward Direction | Forward capability | Reverse Capability
| QNI | NSW to QLD | 410 | 1125
| Terranora | NSW to QLD | 50 | 150
| VIC-NSW | VIC to NSW | 700 | 400
| Heywood | VIC to SA | 650 | 650
| Murraylink | VIC to SA | 220 | 200
| Basslink | TAS to VIC | 478 | 478

## Proportioning factors
TOC
Proportioning factors for Inter-Regional losses
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Losses due to interconnector flow are assigned asymmetrically to regions either side of the interconnector1
| Notional Interconnector | Proportioning Factor | Region applied to
| Queensland - New South Wales (QNI) | 0.68 | New South Wales
| Queensland - New South Wales (Terranora) | 0.66 | New South Wales
| Victoria - New South Wales (VNI) | 0.32 | Victoria
| Victoria - South Australia (Heywood) | 0.78 | Victoria
| Victoria - South Australia (Murraylink) | 0.67 | Victoria
| Tasmania - Victoria (Basslink)2,3 | 1 | Sending end
| Tasmania - Victoria (Marinus Link) | 1 | Sending end
| Queensland - New South Wales (QNI augmentation options)3 | 0.68 | New South Wales
| Victoria - New South Wales (VNI augmentation options)3 | 0.32 | Victoria
| South Australia-New South Wales | 0.5 | New South Wales
1. For derivation of loss factors for existing interconnectors, see Regional Boundaries and Marginal Loss Factors for the 2018-19 Financial Year
2. Deviates from AEMO Feb 2019 ISP assumptions
3. The model applies the same proportioning factors to new interconnector developments as are calculated for the existing interconnectors between the same regions

## Augmentations
TOC
Augmentations
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Long-term modelling assumes the following transmission augmentations between NEM regions. The timings of these augmentations for each scenario are described in the Scenarios tab.
| Interconnector | Option label | Project description | Forward Direction | Notional Limit
[5 empty] | Forward direction | Reverse direction
| QNI (See note 1) | Do nothing | Do nothing | NSW to QLD | 410 | 1125
|  | QNI-Option 3A | New Armidale-Bulli Creek HVAC at 330 kV Install Armidale-Dumaresq and Dumaresq-Bulli Creek additional new 330 kV double circuit line. Uprating of Liddell-Muswellbrook (#83), Muswellbrook-Tamworth (#88) and Liddell-Tamworth (#84) 330 kV lines. Augment existing substations/switching stations at Armidale, Dumaresq and Bulli Creek. | NSW to QLD | 580 | 1355
| VIC-NSW | Do nothing | Do nothing | VIC-NSW | 700 | 400
|  | VIC-NSW Option 1 (Dederang-Lower Tumut path VIC to NSW export) | Install second 500/330 kV 1000 MVA transformer at South Morang. Install a braking resister at Loy Yang or battery storage or FACTS device to increase transient stability. Uprate Dederang-South Morang 330 kV lines and series capacitors. Uprate Canberra-Upper Tumut 330 kV line. | VIC-NSW | 870 | 400
|  | KerangLink | New Sydenham-Ballarat-Bendigo-Kerang-Darlington Point-Wagga 500 kV double circuit line. New Wagga-Snowy 2.0-Bannaby-Wagga 500 kV single circuit line. Cut-in Lower Tumut and Upper Tumut 330 kV line at Snowy 2.0. 2x500/220 kV 1000 MVA transformers at Ballarat, Bendigo and Kerang. 2x500/330 kV 1000 MVA transformers at Darlington Point and Wagga. 2x500/330 kV 1500 MVA transformers at Snowy 2.0. Power flow controller on Bannaby-Sydney West 330 kV line. | VIC-NSW | 2800 | 2200
| VIC - SA (Heywood) | Do nothing | Do nothing | VIC-SA | 650 | 650
| SA-NSW | Project EnergyConnect | New Robertstown-Buronga-Darlington Point 330 kV double circuit line. An additional 330 kV single circuit from Darlington Point-Wagga. A 220 kV single-circuit line from Buronga to Red Cliffs (using double-circuit towers). 2x275/330 kV transformers at Robertstown. 4x330 kV Phase Shift transformers at Buronga. Two new 330/220 kV transformers at Buronga. 50% series compensation on Robertstown and Buronga 330 kV line. Reactive compensation including synchronous condensers (Heywood transfer limit) ((Combined Heywood+(SA-NSW) transfer limit)) | NSW-SA (VIC-SA) ((NSW/VIC-SA)) | 800 (750) ((1300)) | 800 (750) ((1300))
| VIC-TAS | Do nothing | Do nothing | TAS to VIC | 478 | 478
|  | Marinus Link 600 MW, plus augmentation to the AC transmission networks | A 600 MW monopole high voltage direct current (HVDC link), including associated alternating current (AC) transmission network augmentation and connection assets. | TAS to VIC | 1078 | 1078
|  | Marnius Link 1,200 MW, plus augmentation to the AC transmission networks | A 1,200 MW bipolar HVDC link, including associated AC transmission network augmentation and connection assets. | TAS to VIC | 1678 | 1678
|  | Marinus Link 750 MW, plus augmentation to the AC transmission networks | A 750 MW monopole high voltage direct current (HVDC link), including associated alternating current (AC) transmission network augmentation and connection assets. | TAS to VIC | 1228 | 1228
|  | Marinus Link 1,500 MW, plus augmentation to the AC transmission networks | A 1,500 MW bipolar HVDC link, including associated AC transmission network augmentation and connection assets. | TAS to VIC | 1978 | 1978
Notes:
1. For the purpose of describing limits on the NSW-QLD interconnector, NSW generation connected to the 330 kV network north of Armidale (e.g. Sapphire Wind Farm) is assumed to belong to the Queensland region.
2. With a second SA interconnector to Eastern States, VIC-SA Heywood transfer limit would be raised. This is given within brackets ( )
3. Values in double bracket (( )) represent the total transfer level with the existing VIC-SA Heywood interconnector and a new SA interconnector to Eastern States.

## Generator capacity
TOC
Generator capacity
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
| Existing generators |  | Committed Projects from AEMO Feb 2019 ISP 1 |  |  | Advanced VRET Projects 1 |  |  | Additional Committed Projects 1 |  |  | Existing and Committed Battery storage Projects
| Generator | Installed capacity (MW) | Generator | Installed capacity (MW) | Commissioning date | Generator | Installed capacity (MW) | Indicative commissioning date | Generator | Installed capacity (MW) | Indicative commissioning date | Storage | Maximum capacity (MW) | Energy (MWh) | Indicative commissioning date
| Bayswater | 2640 | Barker Inlet | 210 | Aug 2019 | Carwarp Solar | 121.6 | 2020-01-01 | Cherry Tree Wind Farm | 57.6 | 2020-05-01 | Kennedy Energy Park | 2 | 4 | 2019-04-01
| Eraring | 2880 | Bodangora WF | 113.19 | 2018-11-01 | Cohuna Solar | 34.2 | 2019-08-01 | Bomen Solar Farm | 120 | 2020-02-01 | Lakeland | 1.4 | 5.3 | In service
| Liddell | 2000 | Crookwell 2 WF | 91 | 2018-11-02 | Winton Solar | 98.8 | 2020-01-01 | Darlington Point Solar Farm | 275 | 2019-11-01 | Hornsdale | 100 | 129 | In service
| Mount Piper | 1320 | Mt Emerald WF | 180.5 | Oct 2018 | Dundonnel WF | 336 | 2020-07-01 | Brigalow Solar Farm | 34.5 | 2020-03-01 | ESCRI Dalrymple | 30 | 8 | In service
| Vales Point | 1320 | Coopers Gap WF | 453 | Aug 2019 | Mortlake South WF | 157.5 | 2020-07-01 | Teebar Solar One | 52.5 | 2019-07-01 | Ballarat | 30 | 30 | In service
| Callide B | 700 | Kennedy Energy Park WF | 43.2 | Apr 2019 | Berrybank WF | 331.8 | 2020-09-01 | Warwick Solar Farm | 64.2 | 2020-02-01 | Bulgana | 20 | 34 | 2019-08-01
| Callide Power Plant | 900 | Crudine Ridge WF | 135 | 2019-11-01 | [6 empty] | Gannawarra Energy Storage System | 25 | 50 | In service
| Gladstone | 1680 | Crowlands WF | 79.95 | 2019-05-01 | 1. Successful projects for the Victorian Renewable Energy Auction Scheme (VREAS) as announced on Tuesday 11 September, 2018. |  |  | 1. Additional committed project list reflects Generation Information update from May 2019. |  |  | Lake Bonney Battery | 25 | 50 | 2019-05-01
| Kogan Creek | 744 | Lincoln Gap WF | 126 | Apr 2019
| Millmerran | 852 | Willogoleche WF | 119.4 | 2019-03-01
| Stanwell | 1460 | Cattle Hill WF | 144 | Dec 2019
| Tarong | 1400 | Granville Harbour WF | 111.6 | 2019-11-01
| Tarong North | 450 | Mt Gellibrand WF | 132 | 2018-05-01
| Loy Yang A | 2210 | Murra Warra WF | 225.7 | 2019-05-01
| Loy Yang B | 1000 | Bulgana WF | 194 | May 2019
| Yallourn | 1450 | Cherry Tree WF | 58 | May 2020
| Colongra | 724 | Lal Lal Elaine WF | 83.6 | Jul 2019
| Smithfield1 | 170.9 | Lal Lal Yendon WF | 144.4 | Mar 2019
| Tallawarra | 435 | Moorabool WF | 320 | Sep 2019
| Uranquinty | 664 | Stockyard Hill WF | 532 | Dec 2019
| Barcaldine | 37 | Bomen Solar | 120 | Feb 2020
| Braemar | 504 | Daydream Solar | 167.5 | Early 2019
| Braemar 2 | 519 | Darlington Point Solar | 275 | Nov 2019
| Condamine | 144 | Finley Solar | 133 | Oct 2019
| Darling Downs | 644.5 | Hayman Solar | 50 | Early 2019
| Oakey | 282 | Brigalow Solar | 34.5 | Mar 2020
| Roma | 80 | Childers Solar | 56 | Feb 2019
| Swanbank E2 | 385 | Clermont Solar | 92.5 | Oct 2018
| Yabulu | 242 | Collinsville Solar | 42.5 | Aug 2018
| Yarwun | 180 | Haughton Solar | 100 | 2019-11-01
| Somerton | 160 | Kennedy Energy Park Solar | 15 | Apr 2019
| Bairnsdale | 94 | Lilyvale Solar | 100 | Oct 2018
| Jeeralang A | 212 | Limondale 1 Solar | 220 | Apr 2020
| Jeeralang B | 228 | Limondale 2 Solar | 29 | Apr 2019
| Laverton North | 312 | Oakey Solar | 25 | Mar 2019
| Mortlake | 566 | Oakey 2 Solar | 55 | Mar 2019
| Newport | 510 | Rugby Run Solar | 65 | Mar 2019
| Valley Power | 300 | Susan River Solar | 75 | Feb 2019
| Hallett GT | 234.34 | Teebar Solar | 52.5 | Jul 2019
| Dry Creek | 156 | Yarranlea Solar | 102.5 | Aug 2019
| Ladbroke Grove | 80 | Warwick Solar | 64.2 | Feb 2020
| Mintaro | 90 | Beryl Solar | 98.4 | 2019-05-01
| Osborne | 180 | Nevertire Solar | 105 | Jul 2019
| Pelican Point | 529 | Sunraysia Solar | 200 | Dec 2019
| Quarantine | 224 | Bungala 2 Solar | 110 | Jan 2019
| Torrens Island A | 480 | Bannerton Solar | 88 | Oct 2018
| Torrens Island B | 800 | Kiamal Solar | 200 | 2019-05-01
| Bell Bay Three | 120 | Karadoc Solar | 90 | 2018-11-01
| Tamar Valley CCGT | 208 | Numurkah Solar | 100 | 2019-05-01
| Tamar Valley OCGT | 58 | Tailem Bend Solar | 108 | 2019-05-01
| Hunter Valley GT | 50 | Yatpool Solar | 81 | 2019-05-01
| Mackay GT | 34 | Wemen Solar | 87.75 | Oct 2018
| Mount Stuart | 423.5 | 1. Committed project list reflects Generation Information update from January 2019.
| Angaston | 50
| Lonsdale | 20.7
| Port Lincoln | 73.5
| Port Stanvac | 57.6
| Snuggery | 63
| Blowering | 80
| Guthega | 60
| Hume | 29
| Shoalhaven | 240
| Upper Tumut | 616
| Tumut 3 | 1500
| Barron Gorge | 66
| Kareeya | 86.4
| Wivenhoe | 570
| Bogong / Mackay3 | 300
| Dartmouth | 185
| Eildon | 135
| Murray 1 | 950
| Murray 2 | 552
| West Kiewa | 60
| Bastyan6 | 79.9
| Catagunya / Liapootah / Wayatinah4 | 170.1
| Cethana | 85
| Devils Gate | 60
| Fisher | 43.2
| Gordon | 432
| John Butters7 | 144
| Lake Echo | 32.4
| Lemonthyme / Wilmot5 | 81.6
| Mackintosh6 | 79.9
| Meadowbank | 40
| Poatina | 300
| Reece6 | 231.2
| Tarraleah8 | 90
| Trevallyn | 93
| Tribute6 | 82.8
| Tungatinah | 125
| Boco Rock WF | 113
| Capital WF | 140.7
| Cullerin Range WF | 30
| Gullen Range WF | 165.5
| Gunning WF | 46.5
| Silverton WF | 199
| Sapphire WF | 270
| Taralga WF | 106.8
| White Rock WF | 172.5
| Woodlawn WF | 48.3
| Canunda WF | 46
| Cathedral Rocks WF | 66
| Clements Gap WF | 56.7
| Hallett 1 Brown Hill WF | 94.5
| Hallett 2 Hallett Hill WF | 71.4
| Hallett 3 North Brown Hill WF | 132.3
| Hallett 4 The Bluff WF | 52.5
| Hornsdale S1 WF | 102.4
| Hornsdale S2 WF | 102.4
| Hornsdale S3 WF | 112
| Lake Bonney 1 WF | 80.5
| Lake Bonney 2 WF | 159
| Lake Bonney 3 WF | 39
| Mount Millar WF | 70
| Snowtown WF | 98.7
| Snowtown S2 WF | 270
| Starfish Hill WF | 34.5
| Waterloo WF | 130.8
| Wattle Point WF | 90.75
| Musselroe WF | 168
| Woolnorth WF | 140
| Ararat WF | 240
| Bald Hills WF | 106.6
| Challicum Hills WF | 52.5
| Kiata WF | 31.05
| Macarthur WF | 420
| Mortons Lane WF | 19.5
| Mount Mercer WF | 131.2
| Oaklands Hill WF | 67.2
| Portland WF | 151.7
| Salt Creek WF | 54
| Waubra WF | 192
| Yambuk WF | 30
| Yaloak South WF | 28.7
| Broken Hill Solar | 53
| Coleambally Solar | 180
| Griffith Solar | 29.99
| Manildra Solar | 50
| Moree Solar | 56
| Nyngan Solar | 102
| Parkes Solar | 50.5
| Clare Solar | 100
| Darling Downs Solar | 108.5
| Hamilton Solar | 57.5
| Hughenden Solar | 18
| Kidston Solar | 50
| Longreach Solar | 17
| Ross River Solar | 128
| Sun Metals Solar | 124
| Gannawarra Solar | 55
| Bungala one Solar | 110
| Whitsunday Solar | 57.5
1. Smithfield operating as a fast start OCGT from late 2017
2. Swanbank E return to service in 2018
3. Bogong 140MW and Mackay 162MW
4. Catagunya 38MW, Liapootah 48 MW and Wayatinah 84 MW
5. Lemonthyme 31 MW and Wilmot 51 MW
5. Lemonthyme 31 MW and Wilmot 51 MW
6. The capacity of the Anthony Pieman scheme (consisting of Tribute, Mackintosh, Bastyan and Reece) is assumed to be increased by 80 MW for the cases where Marinus Link is commissioned.
7. The capacity of John Butters is assumed to be increased by 20 MW for the cases where Marinus Link is commissioned.
8. The capacity of Tarraleah is assumed to be increased by 150 MW for the cases where Marinus Link is commissioned.

## Generation limits
TOC
Generator modelling assumptions
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
| Coal minimum load |  |  | GPG minimum load1 |  | Capacity factor constraints2
| Generator Station | Generating unit | Minimum Load (MW) | Generator | Minimum Load (MW) | Generator | Max Capacity Factors | End time
| Bayswater | BW01 | 291 | Tallawarra | 190 | Liddell3 | 50% | Date of retirement
| Bayswater | BW02 | 291 | Condamine | 60 | Bayswater | 75% | Date of retirement
| Bayswater | BW03 | 291 | Darling Downs | 109 | Callide B | 70% | Date of retirement
| Bayswater | BW04 | 291 | Yarwun | 120 | Callide Power Plant | 75% | Date of retirement
| Eraring | ER01 | 230 |  |  | Eraring | 60% | Date of retirement
| Eraring | ER02 | 230 | 1. Total power station minimum load conditions reflect assumed efficient use of gas and steam turbines in CCGT operating mode. |  | Gladstone | 50% | Date of retirement
| Eraring | ER03 | 230 |  |  | Kogan Creek | 85% | Date of retirement
| Eraring | ER04 | 230 |  |  | Liddell | 50% | Date of retirement
| Liddell | LD01 | 219 |  |  | Loy Yang A | 85% | Date of retirement
| Liddell | LD02 | 219 |  |  | Loy Yang B | 90% | Date of retirement
| Mount Piper | MP1 | 294 |  |  | Millmerran | 90% | Date of retirement
| Mount Piper | MP2 | 294 |  |  | Mount Piper | 65% | Date of retirement
| Vales Point | VP5 | 251 |  |  | Stanwell | 70% | Date of retirement
| Vales Point | VP6 | 251 |  |  | Tarong | 60% | Date of retirement
| Callide B | CALL_B_1 | 172 |  |  | Tarong North | 70% | Date of retirement
| Callide B | CALL_B_2 | 172 |  |  | Vales Point | 65% | Date of retirement
| Callide Power Plant | CPP_3 | 222 |  |  | Yallourn | 80% | Date of retirement
| Callide Power Plant | CPP_4 | 222
| Gladstone | GSTONE1 | 110 |  |  | 2. Limit based on he average of annual energy from five years 2013-14 to 2017-18 to reflect limitations on annual coal deliveries.
| Gladstone | GSTONE2 | 110 |  |  | 3. AEMO Feb 2019 ISP assumed maximum capacity factor for Liddell
| Gladstone | GSTONE3 | 110
| Gladstone | GSTONE4 | 110
| Kogan Creek | KPP_1 | 350
| Millmerran | MPP_1 | 170
| Millmerran | MPP_2 | 170
| Stanwell | STAN-1 | 183
| Stanwell | STAN-2 | 183
| Stanwell | STAN-3 | 183
| Tarong | TARONG#1 | 140
| Tarong | TARONG#2 | 140
| Tarong | TARONG#3 | 140
| Tarong North | TNPS1 | 178
| Loy Yang B | LOYYB1 | 305
| Loy Yang B | LOYYB2 | 305
| Loy Yang A | LYA1 | 347
| Loy Yang A | LYA2 | 310
| Loy Yang A | LYA3 | 347
| Loy Yang A | LYA4 | 347
| Yallourn | YWPS1 | 210
| Yallourn | YWPS2 | 210
| Yallourn | YWPS3 | 225
| Yallourn | YWPS4 | 228

## Seasonal ratings
TOC
Generator reliability settings
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
| Existing generators1 |  |  | Committed and advanced projects1
| Generator | Summer (MW) | Not summer (MW) | Generator | Summer (MW) | Not summer (MW)
| Bayswater | 2545 | 2665 | Barker Inlet | 210 | 210
| Eraring | 2720 | 2880 | Bodangora WF | 113.19 | 113.19
| Liddell | 1800 | 1800 | Crookwell 2 WF | 91 | 91
| Mount Piper | 1300 | 1400 | Mt Emerald WF | 180.45 | 180.45
| Vales Point | 1320 | 1320 | Coopers Gap WF | 453 | 453
| Callide B | 700 | 700 | Kennedy Energy Park WF | 43.2 | 43.2
| Callide Power Plant | 840 | 840 | Crudine Ridge WF | 135 | 135
| Gladstone | 1680 | 1680 | Crowlands WF | 79.95 | 79.95
| Kogan Creek | 713 | 750 | Lincoln Gap WF | 126 | 126
| Millmerran | 612 | 852 | Willogoleche WF | 119.4 | 119.4
| Stanwell | 1460 | 1460 | Cattle Hill WF | 144 | 144
| Tarong | 1400 | 1400 | Granville Harbour WF | 111.6 | 111.6
| Tarong North | 443 | 443 | Mt Gellibrand WF | 132 | 132
| Loy Yang A | 2144 | 2210 | Murra Warra WF | 226 | 226
| Loy Yang B | 980 | 1150 | Bulgana WF | 194 | 194
| Yallourn | 1420 | 1528 | Lal Lal Elaine WF | 83.6 | 83.6
| Colongra | 648 | 724 | Lal Lal Yendon WF | 144.4 | 144.4
| Smithfield1 | 108.999 | 108.999 | Moorabool WF2 | 320 | 320
| Tallawarra | 378 | 440 | Stockyard Hill WF | 400 | 532
| Uranquinty | 640 | 664 | Bomen Solar | 100 | 100
| Barcaldine | 34 | 37 | Daydream Solar | 150 | 150
| Braemar | 491 | 530 | Darlington Point Solar | 263.333 | 275
| Braemar 2 | 495 | 519 | Finley Solar | 133 | 133
| Condamine | 89.5 | 100 | Hayman Solar | 50 | 50
| Darling Downs | 580 | 633 | Brigalow Solar | 34.5 | 34.5
| Oakey | 282 | 346 | Childers Solar | 56 | 56
| Roma | 54 | 68 | Clermont Solar | 75 | 75
| Swanbank E2 | 350 | 365 | Collinsville Solar | 42.5 | 42.5
| Yabulu | 155 | 161 | Haughton Solar | 100 | 97.3
| Yarwun1 | 180 | 180 | Kennedy Energy Park Solar | 15 | 15
| Somerton | 140 | 160 | Lilyvale Solar | 99.3 | 79.8
| Bairnsdale | 78 | 84 | Limondale 1 Solar | 220 | 220
| Jeeralang A | 189 | 224 | Limondale 2 Solar | 29 | 29
| Jeeralang B | 216 | 255 | Oakey Solar | 25 | 25
| Laverton North | 300 | 340 | Oakey 2 Solar | 55 | 55
| Mortlake | 518 | 584 | Rugby Run Solar | 65 | 65
| Newport | 475 | 510 | Susan River Solar | 75 | 75
| Valley Power | 270 | 336 | Teebar Solar | 52.5 | 52.5
| Hallett GT | 193 | 216 | Yarranlea Solar | 102.5 | 102.5
| Dry Creek | 112 | 143 | Warwick Solar | 64.2 | 64.2
| Ladbroke Grove | 68 | 84 | Beryl Solar | 87 | 83
| Mintaro | 68 | 90 | Nevertire Solar | 105 | 105
| Osborne | 172 | 188 | Sunraysia Solar | 200 | 200
| Pelican Point | 478 | 529 | Bungala 2 Solar | 110 | 110
| Quarantine | 189 | 221 | Bannerton Solar | 88 | 88
| Torrens Island A | 240 | 240 | Kiamal Solar2 | 200 | 200
| Torrens Island B | 780 | 800 | Karadoc Solar | 90 | 90
| Bell Bay Three | 105 | 105 | Numurkah Solar | 100 | 100
| Tamar Valley CCGT3 | 208 | 208 | Tailem Bend Solar | 95 | 95
| Tamar Valley OCGT | 58 | 58 | Yatpool Solar | 81 | 81
| Hunter Valley GT | 30 | 40 | Wemen Solar | 87.75 | 87.75
| Mackay GT | 34 | 34 | Cherry Tree Wind Farm2 | 57.6 | 57.6
| Mount Stuart | 400 | 428 | Bomen Solar Farm2 | 120 | 120
| Angaston | 50 | 50 | Darlington Point Solar Farm2 | 275 | 275
| Lonsdale | 20.7 | 20.7 | Brigalow Solar Farm2 | 34.5 | 34.5
| Port Lincoln | 56 | 73.5 | Teebar Solar One2 | 52.5 | 52.5
| Port Stanvac | 57.6 | 57.6 | Warwick Solar Farm2 | 64.2 | 64.2
| Snuggery | 54 | 63 | Note:
| Blowering | 80 | 80 | 1. "Summer" ratings are 2019/20 summer ratings and "not summer" ratings are 2020 winter ratings
| Guthega | 68 | 68
| Hume | 29 | 0 | 2. Seasonal ratings are absent and nameplate capacities are used.
| Shoalhaven | 240 | 240
| Upper Tumut | 544 | 616
| Tumut 3 | 1800 | 1800
| Barron Gorge | 66 | 66
| Kareeya | 86.4 | 86.4
| Wivenhoe | 570 | 570
| Bogong / Mackay | 300 | 300
| Dartmouth | 165 | 165
| Eildon | 100 | 100
| Murray 1 | 855 | 950
| Murray 2 | 560 | 420
| West Kiewa | 68 | 68
| Bastyan4 | 81 | 81
| Catagunya / Liapootah / Wayatinah | 149.7 | 173.7
| Cethana | 95 | 95
| Devils Gate | 63 | 63
| Fisher | 46 | 46
| Gordon | 370.8 | 370.8
| John Butters5 | 140 | 140
| Lake Echo | 30 | 0
| Lemonthyme / Wilmot | 32 | 86
| Mackintosh4 | 81 | 81
| Meadowbank | 43.8 | 43.8
| Poatina | 342 | 342
| Reece4 | 232 | 232
| Tarraleah6 | 90 | 90
| Trevallyn | 81.9 | 102.8
| Tribute4 | 88 | 88
| Tungatinah | 104.4 | 130.5
| Boco Rock WF | 104.09 | 113.18
| Capital WF2 | 140.7 | 140.7
| Cullerin Range WF2 | 30 | 30
| Gullen Range WF | 165.5 | 165.5
| Gunning WF | 46.5 | 46.5
| Silverton WF | 198 | 198
| Sapphire WF | 187 | 270
| Taralga WF | 106.8 | 106.8
| White Rock WF | 172.5 | 172.5
| Woodlawn WF | 48.3 | 48.3
| Canunda WF2 | 46 | 46
| Cathedral Rocks WF2 | 66 | 66
| Clements Gap WF | 56.7 | 56.7
| Hallett 1 Brown Hill WF | 58.5 | 94.5
| Hallett 2 Hallett Hill WF | 44.2 | 71.4
| Hallett 3 North Brown Hill WF | 81.9 | 132.3
| Hallett 4 The Bluff WF | 32.5 | 52.5
| Hornsdale S1 WF | 100 | 100
| Hornsdale S2 WF | 100 | 100
| Hornsdale S3 WF | 109 | 109
| Lake Bonney 1 WF2 | 80.5 | 80.5
| Lake Bonney 2 WF | 159 | 159
| Lake Bonney 3 WF | 39 | 39
| Mount Millar WF1 | 70 | 70
| Snowtown WF | 98.7 | 98.7
| Snowtown S2 WF | 270 | 270
| Starfish Hill WF2 | 34.5 | 34.5
| Waterloo WF | 130.8 | 130.8
| Wattle Point WF2 | 90.75 | 90.75
| Musselroe WF | 168 | 168
| Woolnorth WF2 | 140 | 140
| Ararat WF | 195 | 240
| Bald Hills WF | 106.6 | 106.6
| Challicum Hills WF2 | 52.5 | 52.5
| Kiata WF | 31.05 | 31.05
| Macarthur WF | 420 | 420
| Mortons Lane WF2 | 19.5 | 19.5
| Mount Mercer WF | 131.2 | 131.2
| Oaklands Hill WF | 41.6 | 63
| Portland WF1 | 151.7 | 151.7
| Salt Creek WF | 54 | 54
| Waubra WF2 | 192 | 192
| Yambuk WF2 | 30 | 30
| Yaloak South WF2 | 28.7 | 28.7
| Broken Hill Solar | 53 | 53
| Coleambally Solar | 150 | 130
| Griffith Solar2 | 29.99 | 29.99
| Manildra Solar | 46.7 | 45
| Moree Solar | 55.2 | 44.4
| Nyngan Solar | 102 | 102
| Parkes Solar | 55 | 53.5
| Clare Solar | 99.3 | 79.8
| Darling Downs Solar | 108.5 | 108.5
| Hamilton Solar | 57.5 | 57.5
| Hughenden Solar2 | 18 | 18
| Kidston Solar | 48.5 | 48.5
| Longreach Solar2 | 17 | 17
| Ross River Solar | 116 | 116
| Sun Metals Solar | 124 | 124
| Gannawarra Solar | 50 | 50
| Bungala one Solar | 110 | 110
| Whitsunday Solar | 57.5 | 57.5
Note:
1. Summer ratings are 2019/20 summer ratings and not summer ratngs are 2020 winter ratings
2. Seasonal ratings are absent and Name plate Capacities are used.
3. Deviates from AEMO Feb 2019 assumptions
4. The seasonal ratings of the Anthony Pieman scheme (consisting of Tribute, Mackintosh, Bastyan and Reece) is assumed to be increased by 80 MW for the cases where Marinus Link is commissioned.
5. The seasonal ratings of John Butters is assumed to be increased by 20 MW for the cases where Marinus Link is commissioned.
6. The seasonal ratings of Tarraleah is assumed to be increased by 150 MW for the cases where Marinus Link is commissioned.

## Generator Reliability Settings
TOC
Generator reliability settings
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
These new entrant technologies are modelled as a single unit per region. Therefore, it is not feasible to implement full or partial outage. The EFOR is used to derate their nameplate capacity year-round.
| Existing generators | [6 empty] | New entrant technologies
| Fuel type | Forced Outage Rate (%) 2 |  | Mean time to repair (hrs) 3 |  | Partial Outage Derating Factor 4 | Expected Forced Outage Rate | Fuel type | Forced Outage Rate (%) |  | Mean time to repair (hrs) |  | Equivalent forced outage rate (%)
|  | Full outage % of time | Partial outage % of time | Full outage | Partial outage |  |  |  | Full outage % of time | Partial outage % of time | Full outage | Partial outage
| Black Coal (Qld) | 2.42% | 13.51% | 53 | 16 | 16.94% | 4.709% | OCGT | 1 | 1 | - | - | 1.1
| Liddell5 | 6.56% | 25.81% | 135 | 19 | 19.98% | 11.72% | CCGT | 2 | 1 | - | - | 2.4
| Black Coal (NSW excluding Liddell)6 | 3.88% | 23.45% | 102 | 16 | 17.76% | 8.045% | Battery Storage (2hrs storage) | 1.5 | 3 | 48 | 96 | 0.021
| Brown Coal (Vic) | 5.34% | 13.32% | 40 | 7 | 19.18% | 7.895% | Pumped hydro | - | - | - | - | 1
| Hydro | 1.58% | 0.01% | 15 | 7 | 17.26% | 1.582%
| Liquid Fuel | 3.56% | 0.28% | 15 | 21 | 26.91% | 3.635%
| Gas-powered steam turbine | 4.58% | 11.25% | 124 | 75 | 22.85% | 7.151%
| CCGT | 1.33% | 0.36% | 17 | 36 | 42.76% | 1.484%
| OCGT | 3.56% | 0.28% | 15 | 21 | 26.91% | 3.635%
1. Gas-powered steam turbines include Newport and Torrens Island A and B
2. The percentage of time per year that a generator is expected to be out of service due to forced outage.
3. The average time take to return a generating unit to service
4. The loss of capacity during a partial outage, relative to generator unit rating. If the outage factor is 20%, the generator will operate at 80% capacity during a partial outage.
5. Based on AEMO Feb 2019 ISP Black Coal (NSW) - until 2022 outage rates
6. Based on AEMO Feb 2019 ISP Black Coal (NSW) - post 2022 outage rates

## Maintenance
TOC
Maintenance rate
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
The percentage of time per year that a generator is expected to be out of service for maintenance. Planned maintenance is coordinated for each of the generator types below so as to avoid periods of high demand and to avoid excessive overlapping maintenance periods that would disrupt the supply demand balance.
Existing generators
| Generator type | % of time out | Planned outages per year | Equivalent average days per year on planned outage
| Black Coal | 5.479% | 1 | 20
| Brown Coal | 5.479% | 1 | 20
| Hydro | 0.274% | 1 | 1
| CCGT | 5.479% | 1 | 20
| OCGT | 1.37% | 1 | 5
| Gas-fired Steam turbine | 0.6849% | 1 | 2.5
| Reciprocating Engine | 1.644% | 1 | 6

## Heat rates
TOC
Heat rates
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Encapsulates the efficiency of thermal generators (as-generated, HHV)
| Existing and committed generators |  | New entrant technologies
| Generator | Heat rate (GJ/MWh) | Technology | Heat rates (GJ/MWh)
| Bayswater | 9.4488 | OCGT | 11.7497
| Eraring | 9.5491 | CCGT | 7.5753
| Liddell | 10.1408
| Mount Piper | 9.2545
| Vales Point | 9.6774
| Callide B | 9.1603
| Callide Power Plant | 9.3023
| Gladstone | 9.4737
| Kogan Creek | 8.802
| Millmerran | 9.2072
| Stanwell | 9.068
| Tarong | 9.2072
| Tarong North | 8.6538
| Loy Yang A | 12.1622
| Loy Yang B | 12.5436
| Yallourn | 13.8996
| Colongra | 11.1455
| Smithfield | 8.3527
| Tallawarra | 6.9903
| Uranquinty | 11.1455
| Barcaldine | 12.7208
| Braemar | 11.8812
| Condamine | 7.2874
| Darling Downs | 7.377
| Oakey | 10.9422
| Roma | 11.8812
| Swanbank E | 7.438
| Yabulu (Townsville) | 7.5949
| Yarwun | 10.3746
| Somerton | 14.876
| Bairnsdale | 10.4956
| Jeeralang A | 15.2542
| Jeeralang B | 15.2542
| Laverton North | 11.5016
| Mortlake | 11.1455
| Newport | 10.2857
| Valley Power | 14.876
| Hallett GT | 14.876
| Barker Inlet | 7.8947
| Dry Creek | 13.6882
| Ladbroke Grove | 11.8812
| Mintaro | 12.7208
| Osborne | 8.1633
| Pelican Point | 7.3469
| Quarantine | 10.7143
| Torrens Island A | 11.4286
| Torrens Island B | 10.7143
| Bell Bay Three | 12.0401
| Tamar Valley CCGT | 7.2874
| Tamar Valley OCGT | 12.7208
| Hunter Valley GT | 12.7208
| Mackay GT | 12.7208
| Mount Stuart | 11.8812
| Angaston | 12.775
| Lonsdale | 7.8947
| Port Lincoln | 12.8114
| Port Lincoln 3 | 12.8114
| Port Stanvac | 7.8947
| Snuggery | 13.4328

## Auxiliary
TOC
Auxiliary load
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Auxiliary load is also called "parasitic load" or "self load" and refers to energy generated for use within power stations
| Existing generators |  | New entrants
| Generator | % auxiliary load | Generator | % auxiliary load
| Bayswater | 6 | OCGT | 1.53
| Eraring | 6 | CCGT | 2.51
| Liddell | 5 | Large scale Solar PV | 2
| Mount Piper | 5 | Battery Storage (2hrs storage) | 4
| Vales Point | 5 | Wind | 2
| Callide B | 9 | Pumped hydro | 1
| Callide Power Plant | 6
| Gladstone | 8
| Kogan Creek | 9
| Millmerran | 6
| Stanwell | 9
| Tarong | 8
| Tarong North | 6
| Loy Yang A | 9
| Loy Yang B | 8
| Yallourn | 10
| Colongra | 1
| Smithfield | 5
| Tallawarra | 3
| Uranquinty | 1
| Barcaldine | 1
| Braemar | 1
| Condamine | 3
| Darling Downs | 6
| Oakey | 1
| Roma | 1
| Swanbank E | 3
| Yabulu (Townsville) | 3
| Yarwun | 2
| Somerton | 1
| Bairnsdale | 1
| Jeeralang A | 3
| Jeeralang B | 3
| Laverton North | 3
| Mortlake | 1
| Newport | 5
| Valley Power | 1
| Hallett GT | 1
| Barker Inlet | 3
| Dry Creek | 1
| Ladbroke Grove | 1
| Mintaro | 1
| Osborne | 5
| Pelican Point | 2
| Quarantine | 5
| Torrens Island A | 5
| Torrens Island B | 5
| Bell Bay Three | 3
| Tamar Valley CCGT | 3
| Tamar Valley OCGT | 1
| Hunter Valley GT | 1
| Mackay GT | 1
| Mount Stuart | 1
| Angaston | 2.5
| Lonsdale | 2.5
| Port Lincoln | 8
| Port Lincoln 3 | 8
| Port Stanvac | 2.5
| Snuggery | 3
| All hydro | 1
| All wind | 1
| All solar | 1

## Emissions
TOC
Emissions
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
| Existing generators |  |  |  | Generic new entrant units and committed projects
| Generator | Combustion emissions (kg/MWh) | Fugitive emissions (kg/MWh) | Total emissions (kg/MWh) | Generator | Region | Combustion emissions (kg/MWh) | Fugitive emissions (kg/MWh) | Total emissions (kg/MWh)
| Bayswater | 865.5122 | 47.1309 | 912.6431 | OCGT | Qld | 624.4845 | 89.2977 | 713.7822
| Eraring | 862.3464 | 47.7966 | 910.1431 | OCGT | NSW | 624.4845 | 158.6209 | 783.1054
| Liddell | 930 | 50.5917 | 980.5917 | OCGT | VIC | 624.4845 | 45.8238 | 670.3083
| Mount Piper | 862.3022 | 46.2162 | 908.5184 | OCGT | SA | 624.4845 | 119.8469 | 744.3314
| Vales Point | 860 | 48.3051 | 908.3051 | OCGT | Tas | 624.4845 | 45.8238 | 670.3083
| Callide B | 920 | 11.3435 | 931.3435 | CCGT | Qld | 394.6595 | 57.5725 | 452.232
| Callide Power Plant | 895.323 | 11.589 | 906.912 | CCGT | NSW | 394.6595 | 102.2669 | 496.9264
| Gladstone | 960 | 11.7614 | 971.7614 | CCGT | VIC | 394.6595 | 29.5438 | 424.2033
| Kogan Creek | 820 | 11.04 | 831.04 | CCGT | SA | 394.6595 | 77.2684 | 471.9279
| Millmerran | 830.1346 | 11.4634 | 841.598 | CCGT | Tas | 394.6595 | 29.5438 | 424.2033
| Stanwell | 860.94 | 11.25 | 872.19 | Barker Inlet | SA | 422.5737 | 80.5263 | 503.1
| Tarong | 860.0221 | 11.4365 | 871.4586
| Tarong North | 832.9647 | 10.7908 | 843.7555 | 1 Generic new entrant units and committed projects emissions are calculated based on unit's heat rates and fuel emissions details given in the GHD 2018 AEMO costs and technical parameter review.
| Loy Yang A | 1150 | 4.8176 | 1154.8176
| Loy Yang B | 1136.0409 | 4.9805 | 1141.0214
| Yallourn | 1310 | 5.5149 | 1315.5149
| Colongra | 640 | 142.56 | 782.56
| Smithfield | 480.9688 | 106.7707 | 587.7395
| Tallawarra | 358.1395 | 89.3952 | 447.5347
| Uranquinty | 581.7116 | 142.56 | 724.2716 | 1
| Barcaldine | 999.9566 | 99.2829 | 1099.2394
| Braemar | 570.4776 | 92.664 | 663.1416
| Condamine | 454.3237 | 56.745 | 511.0687
| Darling Downs | 420.2045 | 57.3809 | 477.5854
| Oakey | 760 | 85.2736 | 845.2736
| Roma | 663.8544 | 92.664 | 756.5184
| Swanbank E | 370 | 57.9523 | 427.9523
| Yabulu | 450 | 59.2122 | 509.2122
| Yabulu Steam Turbine | 450 | 59.2122 | 509.2122
| Yarwun | 532.3129 | 80.9365 | 613.2494
| Somerton | 760 | 57.915 | 817.915
| Bairnsdale | 524.3273 | 40.8812 | 565.2085
| Jeeralang A | 819.9338 | 59.4707 | 879.4045
| Jeeralang B | 819.9338 | 59.4707 | 879.4045
| Laverton North | 745.3812 | 44.7987 | 790.1799
| Mortlake | 530 | 43.4362 | 573.4362
| Newport | 530 | 40.0541 | 570.0541
| Valley Power | 813.6315 | 57.915 | 871.5465
| Hallett GT | 1020 | 154.44 | 1174.44
| Dry Creek | 1200 | 142.56 | 1342.56
| Ladbroke Grove | 530 | 123.552 | 653.552
| Mintaro | 820 | 132.3771 | 952.3771
| Osborne | 460 | 84.6857 | 544.6857
| Pelican Point | 397.2675 | 76.44 | 473.7075
| Quarantine | 688.8094 | 111.15 | 799.9594
| Torrens Island A | 590 | 118.56 | 708.56
| Torrens Island B | 570 | 111.15 | 681.15
| Bell Bay Three | 617.7228 | 46.9614 | 664.6841
| Tamar Valley OCGT | 652.9757 | 49.6414 | 702.6171
| Tamar Valley CCGT | 410.3827 | 28.3725 | 438.7552 | 1
| Hunter Valley GT | 887.1814 | 45.8229 | 933.0043
| Mackay GT | 1000 | 45.8229 | 1045.8229
| Mount Stuart | 955.8648 | 42.768 | 998.6328
| Angaston1 | 940.2 | 73.4 | 1013.6
| Lonsdale1 | 1442 | 49.8 | 1491.8
| Port Lincoln | 1400 | 45.8585 | 1445.8585
| Port Lincoln 3 | 1400 | 45.8585 | 1445.8585
| Port Stanvac | 1442 | 49.8 | 1491.8
| Snuggery | 1400 | 48.3508 | 1448.3508
| All hydro | 0 | 0 | 0
| All wind | 0 | 0 | 0
| All solar | 0 | 0 | 0

## Reserves
TOC
Regional reserve
Primary source: AEMO 2019 ISP Assumptions Workbook v1.0
Each region must have a minimum level of black coal, brown coal, OCGT, CCGT, conventional hydro or interconnector headroom available, but not dispatched in each high demand intervals1. These reserve requirements are used to deliver sufficient capacity to meet reliability requirements. The reserve requirements covers approximately the largest single generating unit.
| Region | Regional Reserve Requirements (MW)
| NSW | 673.2
| QLD | 666.08
| SA | 273
| TAS | 194
| VIC | 498
1. In this context, 'high demand intervals' is defined as the top 1 % demand period for each region.

## Mainland inertia
TOC
Mainland inertia
Primary source: Inertia requirements methodology: Inertia requirements and shortfalls
For each region an inertia constraint was included in the generation development plan to ensure the aggregate total of inertia in each region in each trading interval is sufficient to meet minimum requirements.
| Region | Minimum inertia level (MW.s)
| NSW | 10000
| QLD | 12800
| SA1 | 0
| VIC | 12600
1. For South Australia, the minimum inertia level was sourced from ElectraNet’s calculation of requirements published as part of the South Australian Energy Transformation RIT-T.

## Tasmanian inertia
TOC
Tasmanian inertia
Primary source: TasNetworks
In Tasmania, a customised linear inertia requirement was imposed which accounts for the effect of Tasmanian demand, interconnector flows, seasonal differences in hydro minimum loads and the effect of variable wind production and PSH development. The following equations are enforced as a hard constraint in the model to ensure there is enough inertia in Tasmania in each hour of the forecast:
On export, sum of terms in table below, hard-export column ≥ 390 - 0.5*Tasmanian demand
On import, sum of terms in Table 14, hard-import column ≥ 390 - 0.77*Tasmanian demand
The cost of operation as a synchronous condenser, when required, is computed through an additional constraint with terms using the right two columns of the table. This constraint can violate at a cost of 17 cents/MW.s for that hour long interval.
| Term in inertia constraint equation left-hand side | Hard constraint |  | Soft constraint
|  | Inertia contribution on export (MW.s) | Inertia contribution on import (MW.s) | Inertia contribution on export (MW.s) | Inertia contribution on import (MW.s)
| Tas-Vic flow | -1.7*export flow | -5.3*import flow | -1.7*export flow | -5.3*import flow
| Tasmanian wind | -2.8*dispatch | -4.2*dispatch | -2.8*dispatch | -4.2*dispatch
| Tasmanian PSH | 2*dispatch gen or load | 6.5*dispatch gen or load | 5*dispatch gen or load | 9.5*dispatch gen or load
| Tasmanian PSH | 3*capacity |  | 0
| Gordon | Dec-May: 3*dispatch + 626 Jun-Nov: 3.1*dispatch + 626
| Poatina | 600 |  | 5*dispatch
| Trevallyn | 4.3*dispatch
| John Butters | 1713 |  | 3.9*dispatch
| Tarraleah | 4*dispatch
| Tungatinah | May-Oct: 3.1*dispatch Nov-Apr: 3.2*dispatch
| Lower Derwent | 2*dispatch + 500
| Anthony Pieman | 4*dispatch
| Mersey Forth Upper | 2.8*dispatch
| Mersey Forth Lower | 3.4*dispatch
| Bell Bay | 8.56*dispatch
| Tamar Valley CCGT | 7.72*dispatch
| Tamar Valley OCGT | 7.72*dispatch